## Curated by Zhu et al. (2024)
QA number | QA number2 | Question | Answer
Exercise 1.3.1 | Exercise 1.3.1 | What are the main global drivers for sanitation? | Mainly, good public health by minimising waterborne diseases. In addition, together with access to safe water, it is essential to eradicate poverty, building liveable and prosperous societies.
Exercise 1.3.2 | Exercise 1.3.2 | Describe ancient practices or applications used to recover resources from wastewater. | In China from around 200 BC and up to the 1970s, due to recognition of its fertilizing value, the vast majority of agricultural land was fertilized by human faeces from latrines. In the Indus valley, in the Euphrates region and Greece, sewage and stormwater were being collected in basins outside the cities and used for irrigation purposes and to fertilise crops and orchards from before 2000 BC.
Exercise 1.3.3 | Exercise 1.3.3 | What were the sanitation conditions in the Sanitary Dark Ages? | In the Sanitary Dark Ages, sanitation conditions were rather precarious: waste was simply disposed of in the streets, often by emptying buckets from second-storey windows.
Exercise 1.3.4 | Exercise 1.3.4 | In the Modern Era, when were the first sanitary collection systems installed or put into practice? | In the Modern Era, the first sanitary collection systems were put into practice in several cities, driven by the city dwellers who no longer wanted to put up with the stench. Carts drove through the streets to empty buckets that were full of waste. Farmers located around the cities made use of this practice because they used the 'humanure' to fertilise. However, spillages during transportation and emptying did not help to reduce the smell.
Exercise 1.3.5 | Exercise 1.3.5 | What was the first water-free vacuum collection system implemented? | The Liernur pneumatic sewer system was developed by Mr. Liernur in around 1900 (1882). The system collected toilet water using a vacuum sewer. (added: This system was primarily used in Netherlands)
Exercise 1.3.6 | Exercise 1.3.6 | What were the first biological wastewater treatment systems? | Biological filters were the first biological treatment systems to treat the sewage from towns and cities, mostly in the United States and United Kingdom, and they were introduced between 1893 and 1901.
Exercise 1.3.7 | Exercise 1.3.7 | Why were activated sludge systems named this way? | Based on fill-and-draw wastewater treatment experiments by Ardern and Locket (1914), a highly treated wastewater effluent was produced resembling a sludge. Believing that the working principle was similar to activated carbon, the sludge was therefore called activated sludge.
Exercise 1.3.8 | Exercise 1.3.8 | Why is the Biochemical Oxygen Demand (BOD) determined over a duration of 5 days? | In the first half of the 20th century, the river into which the (treated) wastewater was discharged was considered an integral part of the treatment process. Since the longest time that water spent in the rivers of the UK before it reached the sea is 5 days, this was chosen as the duration of the BOD test.
Exercise 1.3.9 | Exercise 1.3.9 | What was one of the first applications of mathematical modelling in the wastewater treatment field? | A mathematical model presented by Phelps (1944) in the book Stream Sanitation. It was applied to calculate the maximum organic load to a river from the oxygen sag curve. This was to prevent the dissolved oxygen (DO) concentration falling below a minimum value at a defined point downstream the wastewater discharge point.
Exercise 1.3.10 | Exercise 1.3.10 | What led to the introduction of nitrification in wastewater treatment systems? | To decrease the oxygen demand in rivers and the toxic effect that ammonia has on aquatic species.
Exercise 1.3.11 | Exercise 1.3.11 | What were the first treatment systems used to perform nitrification? | Low-loaded trickling filters plants in the USA, Europe and South Africa.
Exercise 1.3.12 | Exercise 1.3.12 | Describe the main disadvantage of the first wastewater treatment systems applied to perform nitrification. | The low-loaded trickling filters failed to nitrify consistently throughout the year, in particular due to the lower temperatures experienced in winter.
Exercise 1.3.13 | Exercise 1.3.13 a | What is eutrophication? | Eutrophication is the excessive growth of algae and other plants in surface water bodies due to the fertilizing effect of nitrogen (N) and phosphorus (P).
Exercise 1.3.13 | Exercise 1.3.13 b | Why is eutrophication an undesirable process in receiving waters? | Eutrophication is an undesirable process: during the day there is a large photosynthetic production, and during the night oxygen depletion occurs and therefore plants and fish die off. The decaying biomass contributes even more to oxygen shortage. In addition, cyanobacteria (which also proliferate during the eutrophication processes) generate toxins that have a major deleterious effect on aquatic organisms and this affects the use of the water body as a source of (potable) water. Consequently, eutrophication may decrease water availability, affecting key sectors and activities (such as food production, industry and even tourism and recreation).
Exercise 1.3.14 | Exercise 1.3.14 | What was and continues to be one of the main applications of the Monod kinetic expression? | Its application to describe the growth rate of bacteria as a function of the substrate concentration. In particular, in 1964, Downing et al. used it to show that the nitrification process depends on the maximum specific growth rate of autotrophic organisms (Downing et al., 1964). This demonstrated that their growth is slower than that of ordinary heterotrophic organisms and that biological wastewater treatment systems had to be designed and operated at sludge ages long enough to enable the growth of autotrophic organisms to achieve consistently low effluent ammonia concentrations.
Exercise 1.3.15 | Exercise 1.3.15 | What supported the development of the nitrification-denitrification processes? | The advanced studies on bioenergetics carried out by McCarthy (McCarthy, 1964). He showed that nitrate generated by the nitrification process could be used as an alternative for oxygen by certain heterotrophic organisms and it is thereby converted to dinitrogen gas. Unaerated sections were included in activated sludge systems to induce denitrification, thus saving aeration energy and removing nitrogen.
Exercise 1.3.18 | Exercise 1.3.18 | Describe the main characteristics of the Pasveer ditch system developed in 1959. | This was a simple and economical system solely composed of one treatment tank with no primary settler or secondary settling tank. It followed the fill-and-draw principle developed by Ardern and Locket in the UK in 1914 (Pasveer, 1959). Moreover, if operated with continuous feeding, it was able to achieve simultaneous nitrification and denitrification. These continuously operated oxidation ditch and carrousel systems evolved from the Pasveer system but included a secondary settling tank.
Exercise 1.3.19 | Exercise 1.3.19 | Why is it important to also remove phosphorus in order to prevent eutrophication? | Because phosphorus has been identified as the main enabling element for eutrophication in several ecosystems, removing only nitrogen is therefore insufficient to prevent it. Microorganisms (especially blue- green algae) can use nitrogen gas as a nitrogen source, and therefore phosphorus is the main growth-limiting compound in surface water.
Exercise 1.3.20 | Exercise 1.3.20 | Explain why it is assumed that the Enhanced Biological Phosphorus Removal (EBPR) process was discovered by accident. | Because the first indication of the occurrence of EBPR in activated sludge systems was observed by Srinath et al. in India (Srinath et al., 1959) in a treatment plant where the aeration in the first stage of the activated sludge plant was compromised. They merely noticed that the sludge showed an excessive uptake of phosphorus (beyond that required for biomass synthesis) when it was aerated. It was also shown that it was a biological process since it was oxygen-dependent and it was inhibited by toxic substances.
Exercise 1.3.22 | Exercise 1.3.22 | What led to the development of anaerobic wastewater treatment technologies? | The development of anaerobic wastewater treatment technologies was motivated by the energy crisis experienced in the 1970s together with an increased demand for industrial wastewater treatment. Furthermore, the invention of upflow anaerobic sludge blanket reactors (UASB) by Lettinga and colleagues (Lettinga et al., 1980) led to a breakthrough in anaerobic treatment. Not only was this technology feasible for industrial wastewater treatment but anaerobic treatment of low-strength municipal wastewater could also be efficiently introduced in tropical regions of South America, Africa and Asia.
Exercise 1.3.23 | Exercise 1.3.23 | Describe the factors leading to the development of the latest biofilm-based treatment systems. | The main cause was the need to develop more compact wastewater treatment plants since rapid urbanization has led to a lower availability of land. Also industries, often with land limitations, started to treat their own wastewater. This caused the development of a whole range of new biofilm-based processes such as biological aerated filters, fluid-bed reactors, moving-bed bioreactors and granular sludge processes, among others.
Exercise 1.3.24 | Exercise 1.3.24 | How is the solid-liquid separation process carried out in a membrane bioreactor (MBR) system? | The solid-liquid separation process is carried out by a membrane (either submerged in the main aerobic reactor of the MBR system or located externally). The membrane enables the solids to be retained and produces a clarified treated effluent (Yamamoto et al., 1989).
Exercise 1.3.25 | Exercise 1.3.25 b | What removal processes does Nereda® process perform? | To minimize costs, it is a sequencing technology based on the fill-and-draw principles of Ardern and Locket (1914) and Pasveer (1959) so all the biological conversion and settling processes occur in one single reactor.
Exercise 1.3.26 | Exercise 1.3.26 | What was the reason to upgrade existing wastewater treatment plants by carrying out the removal of nutrients in the sludge treatment line? | One of the main factors was the need to upgrade existing plants in order to comply with the new stricter effluent discharge standards instead of building new treatment systems. Thus, it was observed that considerable nitrogen and phosphorus concentrations were released in the sludge handling facilities, which returned to the main-stream wastewater treatment line through internal recycle flows. The development and implementation of different side-stream processes, which take advantage of the particular characteristics of the side-stream streams (e.g. highly concentrated, higher temperatures and lower flow rates), promoted and facilitated the cost-effective removal of nitrogen and phosphorus. Processes such as the high activity ammonium removal over nitrite (SHARON®), the anaerobic ammonia oxidation (ANAMMOX®) and Crystalactor® (for improved nitrogen removal and mineral crystallization for phosphorus precipitation, recovery and reuse), are some of the technologies that have contributed to these developments.
Exercise 1.3.27 | Exercise 1.3.27 | List at least five resources that can be recovered or generated from wastewater. | In view of an increasing interest in the last decade, in addition to the recovery of water and biogas, cellulose, hydrogen, polyhydroxyalkanoates, nitrogen, phosphates, proteins, extracellular polymers, and even heat, have been identified as recoverable resources from wastewater.
Exercise 1.3.28 | Exercise 1.3.28 | What is the main advantage of the development and implementation of instrumentation, control and automation (ICA)? | The main advantage is to facilitate the operation of existing wastewater treatment plants increasing their reliability to meet stricter effluent standards. It also contributes to a reduction in the operational costs, savings, and recovery of resources.
Exercise 1.3.29 | Exercise 1.3.29 | Why have disinfection and the removal of micropollutants of emerging concern received an increasing amount of interest in recent decades? | Because water reclamation and reuse has been seen as an alternative in order to alleviate water scarcity. Thus, for instance, UV and ozonation technologies (among others) have become increasingly interesting as disinfection processes as well as for the removal of pollutants of emerging concern.
Exercise 1.3.30 | Exercise 1.3.30 a | Describe the main driver behind the use of seawater for toilet flushing. | The main driver is coping with water scarcity and the need to save fresh water through the search and implementation of alternative water sources for non-potable water related activities.
Exercise 1.3.30 | Exercise 1.3.30 b | Describe the advantages of the use of seawater for toilet flushing. | This practice relies on the fact that, in current sanitation systems, on average at least one third of the water consumed in a household is used for toilet flushing and does not require water of drinking quality.
Exercise 1.3.25 | Exercise 1.3.25 a | What is the Nereda® process ? | The Nereda® process is an aerobic granular sludge technology that allows a more efficient and compact removal of nutrients.
Exercise 3.4.1 | Exercise 3.4.1 a | What is the difference between the concepts of person load (PL) and population equivalent (PE)? | PE is a standard unit referring to the typical contribution of an individual to the wastewater load (in terms of flow rate or BOD load). PE can also be used to quantify the load of industrial wastewater streams. PL refers to the actual contribution of persons living in the sewer catchment connected to the WWTP of concern. The PL therefore varies between regions whereas PE (a standard unit) does not.
Exercise 3.4.1 | Exercise 3.4.1 b | What do person load (PL) and population equivalent (PE) have in common? | Both PE and PL are related to the load of a WWTP and based on average contributions, which are obtained from long-term data.
Exercise 3.4.10 | Exercise 3.4.10 a | What are the sources of internal loads in a wastewater treatment plant? | Internal loads: Supernatant from sludge thickener (before digestion) and digester; Reject water from dewatering unit (following sludge digestion); Filter washing water.
Exercise 3.4.10 | Exercise 3.4.10 b | Describe the main characteristics of sources of internal loads in a wastewater treatment plant. | Supernatant from sludge thickener (before digestion) and digester – high ammonia concentrations; Reject water from dewatering unit (following sludge digestion) – high concentration of organic soluble components and soluble nitrogen; Filter washing water – high hydraulic load and also high suspended solids concentration.
Exercise 3.4.14 | Exercise 3.4.14 | List and describe the different wastewater sampling procedures. | Grab sampling is the collection of a single sample or individual samples in a recipient at a specific time instant. • Time proportional sampling is a type of composite sampling, wherein a number of samples are taken at regular time intervals and are then combined in one final sample. • Flow proportional sampling is another type of composite sampling, wherein a number of samples are taken for each specific volume of wastewater flow. Another method of flow proportional sampling is to take samples at a constant time interval with volumes of the samples proportional to the flow.
Exercise 4.4.1 | Exercise 4.4.1 | Explain the fate of the biodegradable soluble and particulate organics in a CAS system. | Both the biodegradable soluble and the biodegradable particulate organics will be mostly converted into new biomass cells. The difference is that the biodegradable soluble organics are rapidly converted whereas the biodegradable particulate organics get enmeshed in the sludge flocs, being slowly hydrolysed prior to their conversion into new biomass.
Exercise 4.4.2 | Exercise 4.4.2 | Explain the fate of the unbiodegradable soluble and particulate organics in a CAS system. | Soluble unbiodegradable organics cannot be removed either biologically (e.g., for the synthesis of new cell biomass) or physically (e.g., because they are soluble and do not get enmeshed in the sludge flocs). Thus, soluble unbiodegradable organics leave through the effluent of the activated sludge plant. Unbiodegradable particulate organics cannot be removed biologically but are enmeshed in the sludge flocs, accumulating in the system and ultimately being removed via the waste of activated sludge.
Exercise 4.4.3 | Exercise 4.4.3 | Explain what the sources of inorganic or fixed suspended solids are in a conventional activated sludge system. | Inorganic suspended solids can be present in the influent wastewater depending on the origin and quality of the wastewater (e.g., if hard water is supplied to the water network or if saline water intrusion or groundwater infiltration occurs). In addition, active biomass cells need inorganic compounds (e.g., micronutrients) to carry out their microbial metabolism and therefore they accumulate in the activated sludge plant as a function of the active biomass.
Exercise 4.4.4 | Exercise 4.4.4 | Explain why a certain percentage of the influent nutrient concentrations are removed in a fully aerobic activated sludge plant even if it is not designed for the removal of nutrients. | Ordinary heterotrophic organisms, the dominant organisms in activated sludge systems, require (macro-) nutrients, mostly nitrogen and phosphorus, to synthesize new biomass cells. They cover these biomass nutrient requirements by consuming the nutrients present in the influent wastewater.
Exercise 5.4.3 | Exercise 5.4.3 | In the design and operation of nitrification systems, what is the meaning of the SRTmin? | It is the minimum SRT required to allow the growth of nitrifying organisms and, consequently, the minimum SRT needed to achieve nitrification.
Exercise 5.4.4 | Exercise 5.4.4 | Why is a safety factor used to calculate the SRTmin? | A safety factor is used to ensure that nitrification is satisfactorily achieved; otherwise, the wastewater treatment plant may be designed and operated at the edge of the nitrification process where a minor variation in the applied SRT could limit it. Also, it compensates for potential load variations during the day as well as potential variations when controlling the SRT.
Exercise 5.4.5 | Exercise 5.4.5 a | In an activated sludge plant that performs the nitrification process, what is the fate of the free and saline ammonia (FSA) concentrations (NH4 + and NH3)? | The FSA is bioavailable for biomass synthesis and nitrification.
Exercise 5.4.5 | Exercise 5.4.5 b | In an activated sludge plant that performs the nitrification process, what is the fate of the biodegradable organic N compounds? | The biodegradable organic N compounds are hydrolysed and their nitrogen contents are released becoming, together with the FSA, bioavailable for biomass synthesis and nitrification.
Exercise 5.4.6 | Exercise 5.4.6 | Even if the applied SRT is longer than the SRTmin, why cannot full nitrification (a zero effluent FSA concentration) be achieved in a fully aerated activated sludge system? | The nitrification process is highly dependent on the kinetics; as such, the half-saturation concentration on FSA (KANO,T) plays a major role at low concentrations (< 4 mgN/l) slowing down and limiting the FSA oxidation as the FSA concentration decreases, avoiding a full FSA oxidation being reached.
Exercise 5.4.7 | Exercise 5.4.7 | If a fully aerated WWTP does not nitrify, what would be the expected Ne and TKNe concentrations? | The expected Ne will be identical to TKNe and therefore composed of the total influent N (Ni) minus the N concentration used for biomass synthesis (Ne = Ni - Ns).
Exercise 5.4.8 | Exercise 5.4.8 | If a fully aerated WWTP is able to nitrify, what would be the expected Ne and TKNe concentrations? | Since there is no denitrification (the plant is fully aerated), the expected Ne will be composed of the total influent N (Ni) minus the N concentration used for biomass synthesis (Ne = Ni – Ns) which is identical to the sum of SNHx,e plus Nous,e and the nitrate generated SNO3,e (Ne = SNHx,e + Nous,e + SNO3,e). This happens because the nitrate generated is not removed via the denitrification process. However, TKNe will be equal to the N fractions that cannot be oxidized (either because of kinetic limitations or because they are unbiodegradable soluble): TKNe = SNHx,e + Nous,e.
Exercise 5.4.9 | Exercise 5.4.9 | What is the meaning of the fx,max in an activated sludge nutrient removal plant ? | It is the maximum unaerated mass zone that can be implemented in an activated sludge nutrient removal plant without hampering the nitrification process.
Exercise 5.4.10 | Exercise 5.4.10 | What is the influence of temperature on the nitrification process in terms of the maximum growth rate? | Temperature plays a major role in nitrification; every increase of 6 °C doubles the maximum growth rate and every decrease of 6 °C halves it.
Exercise 5.4.11 | Exercise 5.4.11 | What are the advantages of implementing a pre-denitrification instead of a post-denitrification configuration? | A pre-denitrification configuration can have a higher denitrification potential than a post-denitrification system. This happens because it can utilize both the readily and the slowly biodegradable organics for denitrification (as well as of the endogenous denitrification), while a post-denitrification can only utilize the slowly biodegradable organics and the endogenous denitrification. Furthermore, the denitrification rate on the readily biodegradable organics is more than 7 times faster than the other two (0.720 compared to 0.101 and 0.072 mg NO3--N/mgVSS.d, respectively).
Exercise 5.4.12 | Exercise 5.4.12 | What is the meaning of the fx1,min in biological wastewater treatment? | fx1,min is the minimum unaerated mass fraction required to utilize all the readily biodegradable organics for denitrification in a pre-denitrification configuration.
Exercise 5.4.13 | Exercise 5.4.13 | What is the a-optimum internal recycle ratio in activated sludge? | In an activated sludge pre-denitrification configuration, it is the internal recycle ratio from the aerobic to the anoxic mass fraction that maximizes the denitrification process by recirculating the optimal nitrate load that can be denitrified.
Exercise 5.4.14 | Exercise 5.4.14 | What is the a-practical internal recycle ratio in activated sludge? | Mathematically, an a-optimal recycle ratio can have values higher than 5.0. However, these may lead to high operational costs and, from a practical perspective, may not be applicable. Consequently, an a-recycle ratio with a value of 5.0 is suggested as the maximum or practical a-recycle ratio that can provide a satisfactory denitrification removal while remaining applicable and feasible to implement.
Exercise 5.4.15 | Exercise 5.4.15 | From a process performance perspective, what are the reasons why the value of the a-optimum internal recycle ratio could be higher than that of the a-practical internal recycle ratio? | During the design process, a-optimum values higher than the a-practical value of 5.0 are obtained when the denitrification potential (Dp1) is considerably higher than the nitrification capacity (NITc). For instance, to decrease an a-optimum value, the Dp1 can be decreased by shortening the anoxic mass fraction fx1 (provided it remains higher than fx1,min).
Exercise 5.4.16 | Exercise 5.4.16 | What are the disadvantages of applying an internal a-recycle ratio higher or lower than the a-optimum ratio? | To apply an internal a-recycle ratio either higher or lower than the a-optimum results in a suboptimal denitrification efficiency. An a-recycle higher than the optimal will increase the intrusion of oxygen into the anoxic mass fraction, decreasing the availability of biodegradable organics for denitrification (and also increasing the operational costs). Meanwhile, an a-recycle ratio lower than the optimal will recycle a lower nitrate load than the one that could be denitrified, making a suboptimal use of the denitrification potential of the system.
Exercise 5.4.17 | Exercise 5.4.17 | Why is the oxygen required to oxidize ammonium to nitrate higher than the oxygen equivalents that can be recovered from the denitrification process? | Because in the nitrification process the oxidation of FSA loses 8 electrons which are passed to oxygen, while the denitrification process only recovers 5 electrons donated from the biodegradable organics. As such, the nitrification process consumes 4.57 mgO2/mgFSA oxidized while the denitrification process recovers 2.86 mgO2/mgNO3- denitrified. In addition, activated sludge systems rarely achieve denitrification efficiencies higher than 90 %, decreasing even further the ‘recovery of oxygen’.
Exercise 5.4.18 | Exercise 5.4.18 | Why cannot all the alkalinity consumed in the nitrification process be recovered during the denitrification process? | Because the nitrification process generates two protons per mol of FSA oxidized (resulting in an alkalinity consumption of 7.14 mg alkalinity as CaCO3/mg FSA) while the denitrification process only recovers 1 proton per mol of nitrate denitrified (recovering 3.57 mg alkalinity as CaCO3/mg NO3-N).
Exercise 5.4.19 | Exercise 5.4.19 | What is a balanced MLE system? | A balanced MLE system is a system whose unaerated mass fraction fx1 is equal to fx,max and the a-optimum ratio is equal to the a-practical ratio. These conditions optimize the design and operation of the nitrogen removal activated sludge plant. This can be achieved because: 1) The applied SRT is the minimum required to achieve nitrification, avoiding the necessity to have larger tanks and higher oxygen consumption requirements. 2) The maximum denitrification potential is used, avoiding any unused anoxic mass fraction, which also contributes to decreasing the volume of the system. 3) It promotes the recycle of an optimal nitrate load (due to a-optimal), making an optimal use of the denitrification potential. 4) It applies the a-practical internal recycle ratio which makes it possible to reach the minimum nitrate concentration in the effluent of the plant.
Exercise 5.4.22 | Exercise 5.4.22 | What is the SHARON process? | SHARON stands for Single reactor High Ammonium Removal Over Nitrite. Briefly, it refers to the nitritation process or oxidation of ammonium to nitrite (and not to nitrate). This can be achieved in effluents that contain high ammonium concentrations at temperatures higher than 25-30 °C by applying short solid and hydraulic retention times (of approximately 1-1.5 d). High salinity can also contribute to this. These conditions tend to favour the activity of ammonium oxidizing organisms while limiting that of nitrite oxidizing organisms, leading to nitrite accumulation. If the denitrification (or denitritation process) takes place on nitrite, considerable savings in oxygen, carbon requirements and sludge generation can be achieved.
Exercise 5.4.23 | Exercise 5.4.23 | What is the ANAMMOX process? | The ANAMMOX process stands for anaerobic ammonium oxidation. It is an autotrophic removal process of ammonium by anammox organisms using nitrite. The main advantages are that it does not require organic carbon to drive this process, that only 50% of the ammonium has to be oxidized to nitrite, and that there is a low biomass yield. These features make it a sustainable process for ammonium removal from wastewater.
Exercise 5.4.24 | Exercise 5.4.24 | What is the BABE process? | The BABE process is a bioaugmentation process that can be implemented in plants that treat their wastewater aerobically in activated sludge systems and their excess of sludge in anaerobic digesters. Thus, a fraction of the sludge recycled from the secondary settling tanks back to the aerobic reactors can be mixed and aerated with a flow of (warm) reject water (i.e. in a 1:1 ratio) generated by the anaerobic digesters (usually operated at mesophilic temperatures ~30-35 °C). The advantages of this application are that it boosts the growth of indigenous nitrifiers, contributing to an increase in the oxidation of ammonium when the nitrifiers return to the mainstream treatment line. This makes it possible to improve the nitrification process even at lower environmental temperatures. (bio-augmentation batch enhanced)
Exercise 5.4.25 | Exercise 5.4.25 | An activated sludge plant treats a municipal wastewater that has an influent CODi/Ni ratio higher than 12. The plant has a 4-stage Bardenpho configuration. A gravity thickener is used to thicken the surplus sludge which is later treated in an anaerobic digester. Sludge waste from the anaerobic digester is dewatered in a centrifuge, where a poly-electrolyte is added to enhance the dewatering process, prior to disposal for incineration. The plant struggles to meet the Ne standard of 10 mg/l, particularly during winter when the sewage temperature drops below 10 °C and free and saline ammonia (FSA) comprises most of the nitrogen present in the effluent. Land/space is limited. Supernatant and reject water from the sidestream processes (the thickener and centrifuge) is recirculated to the anoxic stage of the plant. SRT was extended until the maximum capacity of the secondary clarifiers was reached, resulting in a MLSS concentration of around 6,500 mg/l in the aerobic tank, but no improvement was observed in the nitrogen removal efficiency. Explain briefly which sidestream process you would select (out of SHARON, SHARON-ANAMMOX and BABE) to achieve satisfactory nitrogen removal. | Nitrification is limited because of the high free and saline ammonia concentration observed in the effluent. The SRT was extended at the maximum without observing any results. Thus, to install the BABE process in the recirculation line could be an option to augment the concentration of nitrifiers in the system, helping to improve the nitrification process.
Exercise 5.4.26 | Exercise 5.4.26 | After certain industrial plants started to discharge their effluent into the sewer network, the CODi/Ni ratio of a municipal wastewater treated in an activated sludge system decreased to around 7 and the Ne standard of 10 mg/l is not met during most of the year (nitrate being the most abundant N compound present in the effluent). The plant has a MLE configuration. Surplus sludge is thickened (in a gravity thickener), treated in an anaerobic digester, and thereafter dewatered in a centrifuge (where a poly-electrolyte is added for dewatering purposes) prior to disposal for incineration. Supernatant and reject water from the sidestream processes (the thickener and centrifuge) is recirculated to the anoxic stage of the plant. Secondary clarifiers are at their normal capacity contributing to keep a MLSS concentration of around 4,500 mg/l in the aerobic tank. Which sidestream process would you select (out of SHARON, SHARON-ANAMMOX and BABE) to achieve satisfactory nitrogen removal in this plant? | Nitrate is produced so nitrification is not limiting, but the denitrification appears to be the bottleneck. The relatively low CODi/Ni ratio (~7.0) suggests that there is not enough carbon available for denitrification, supporting the initial hypothesis that denitrification is limited. Furthermore, the supernatant from the thickener and reject water are recirculated to the anoxic stage, meaning that any COD present in this internal stream is not sufficient. An adequate alternative could be to implement either the SHARON process or the SHARON-ANAMMOX process. If the SHARON process is implemented, the carbon requirements could decrease since the denitrification over nitrite requires less carbon source (but an external carbon source may still be needed). Alternatively, the SHARON-ANAMMOX process can help to achieve full nitrogen removal without requiring any addition of organic carbon.
Exercise 5.4.27 | Exercise 5.4.27 | After the expansion of the sewer network, a MLE plant struggles to meet the Ne standard of 10 mg/l during most of the year. Ammonium is the major N compound present in the effluent. The plant treats municipal wastewater with an influent CODi/Ni ratio of approximately 10. A gravity thickener is used to thicken the surplus sludge which is later dewatered on sludge drying beds and used for agricultural purposes. Supernatant from the thickener and sludge drying beds is recirculated to the anoxic section of the MLE system. As a potential solution, the SRT was extended without observing any improvement in the nitrogen removal efficiency. Given the previous conditions, which sidestream process would you select (out of SHARON, SHARON-ANAMMOX and BABE) to achieve satisfactory nitrogen removal in this system? | Nitrification is the limiting step due to the high ammonium concentration. The CODi/Ni ratio of 10 indicates that there is sufficient COD available for denitrification. Because NH3 is the counterion in the sludge reject water (since it is produced in the sludge drying beds), then an option could be the SHARON process to achieve partial nitrification and denitrify on the nitrite concentration available. This will favour the nitrification process and also reduce the aeration and carbon requirements.
Exercise 6.4.2 | Exercise 6.4.2 | In what form do PAO store internally the phosphorus that they remove? | Polyphosphate
Exercise 6.4.3 | Exercise 6.4.3 | Which factors are known to trigger the competition between PAO and GAO? | Several factors exist that affect the PAO-GAO competition, including: (i) type of VFA, (ii) dissolved oxygen concentration, (iii) pH, and (iv) temperature.
Exercise 6.4.4 | Exercise 6.4.4 | What is the main selection pressure that favours the proliferation of PAO in an EBPR system? | There are several factors, but the most accepted is the P/VFA ratio fed. A higher ratio (e.g., P/VFA>0.5) would give rise to PAOs whereas a lower one (i.e., P/VFA < 0.5) to GAOs.
Exercise 6.4.5 | Exercise 6.4.5 | What are the main characteristics of EBPR systems? | The selective growth of biomass that is capable of removing phosphorus beyond its anabolic requirements by accumulating intracellular polyphosphate reserves.
Exercise 6.4.6 | Exercise 6.4.6 | List the two most common PAO found in full-scale EBPR WWTPs. | Candidatus Accumulibacter and Tetrasphaera.
Exercise 6.4.7 | Exercise 6.4.7 | Explain the classical definition for the PAO phenotype. | Anaerobic P release with PHA storage, aerobic (or anoxic) P uptake and growth from PHA oxidation.
Exercise 6.4.8 | Exercise 6.4.8 | Explain the general metabolism of a PAO phenotype. | In the absence of any electron acceptor, PAO sequesters and intracellularly stores RBCOD as PHA. The energy and redox sources are provided by utilizing intracellular polymers (poly-P and glycogen). Thereafter, when exposed to the presence of electron acceptors (e.g., nitrate or oxygen), PAO oxidizes the previously stored PHA to replenish their intracellular polymer pools (poly-P and glycogen) and to grow.
Exercise 6.4.9 | Exercise 6.4.9 | Why is phosphorus the key element to remove from wastewater to minimize the occurrence of eutrophication in surface water bodies? | Unlike nitrogen (which can be fixed from the atmosphere), phosphorus can only be available for the microorganisms when it is dissolved in water.
Exercise 6.4.10 | Exercise 6.4.10 | What is the principal source of ATP for anaerobic organic carbon uptake by PAO? | Polyphosphate hydrolysis
Exercise 6.4.11 | Exercise 6.4.11 | Name two ways that NADH can be produced anaerobically within PAO. | Glycogen degradation and the TCA cycle.
Exercise 6.4.12 | Exercise 6.4.12 | Why is more phosphorus stored aerobically than released anaerobically by PAO? | PAO cells grow aerobically; the increase in cell quantity (growth) leads to higher levels of P taken up aerobically than released anaerobically.
Exercise 6.4.13 | Exercise 6.4.13 | What determines the type of PHA stored by PAOs? | The type of VFA stored determines the types of PHA stored: a higher consumption of acetate (HAc) leads to a higher accumulation of poly-β-hydroxybutyrate (PHB), whereas a higher consumption and storage of propionate (HPr) leads to a higher generation and accumulation of poly-β-hydroxyvalerate (PHV) and poly-β- hydroxy-2-methylvalerate (PH2MV).
Exercise 6.4.14 | Exercise 6.4.14 | How does pH affect the VFA uptake by PAOs? | VFAs require energy to be transported through the cell membrane, which is often provided by polyphosphate hydrolysis and glycogen consumption. As such, the energy requirements for VFA uptake increase when the pH increases.
Exercise 6.4.15 | Exercise 6.4.15 | What is the main difference in terms of ATP and reducing power generation between the glycogen degradation and polyphosphate hydrolysis processes? | During glycogen degradation ATP and NADH are formed, while during the hydrolysis of poly-P only ATP is generated.
Exercise 6.4.16 | Exercise 6.4.16 a | What are the advantages of the modified UCT configuration compared to the 5-stage Bardenpho configuration? | The modified UCT configuration tends to minimize the intrusion of electron acceptors into the anaerobic stage, which can result in a stable and robust EBPR process.On the other hand, the 5-stage Bardenpho has a relatively simpler configuration that can also lead to lower effluent nitrate concentrations (e.g., by adding external carbon sources in the secondary anoxic reactor).
Exercise 6.4.16 | Exercise 6.4.16 b | What are the disadvantages of the modified UCT configuration compared to the 5-stage Bardenpho configuration? | Compared to the 5-stage Bardenpo configuration, it has a lower anaerobic solids concentration and tends to have a more complex operation. The 5-stage Bardenpho may have higher construction and operation costs (since the system requires 5 different tanks or stages and due to the purchase of the external carbon source).
Exercise 6.4.17 | Exercise 6.4.17 | What is the source of organic carbon metabolized by PAO in S2EBPR systems? | Hydrolysis and fermentation of RAS producing soluble organic carbon (e.g., VFA).
Exercise 6.4.18 | Exercise 6.4.18 | What is the function of the anaerobic zone in EBPR systems? | Conversion of fermentable COD into VFA, allowing PAOs to intracellularly store the influent and generated VFA.
Exercise 6.4.19 | Exercise 6.4.19 | Explain why recycling nitrate or oxygen into the anaerobic reactor can destabilize the EBPR process. | With nitrate present in the anaerobic zone, denitrifiers compete for organic carbon uptake with PAO and fermenters, leading to less carbon source taken up by PAO anaerobically for PHA production, and less aerobic P uptake from PHA oxidation.
Exercise 6.4.20 | Exercise 6.4.20 | Name two conditions that can promote the growth of glycogen-accumulating organisms. | A combination of high temperature, low pH, high influent COD/P ratio.
Exercise 6.4.21 | Exercise 6.4.21 | How does a primary settler affect the EBPR process? | The sedimentation and removal of influent biodegradable particulate COD (XS,i) in the primary settling tank (PST) would reduce the flux of biodegradable COD entering into the activated sludge system. This decreases the concentration of fermentable of COD converted, while the influent orthophosphate concentration (the most abundant P compound) will not be affected by the PST. Thus, less active biomass grows in the system and less fermented COD can be generated in the anaerobic reactor (SF,i,conv). Consequently, the COD flux to PAOs will tend to be lower (FSs,PAO), decreasing the PAO biomass, and meanwhile the influent orthophosphate concentration will be similar with or without the PST.
Exercise 6.4.22 | Exercise 6.4.22 | Discuss the effect of long SRT (>20 d) on EBPR systems. | Long SRT leads to lower active biomass. Thus, the poly-P content in PAO biomass would be higher and could reach their maximum storage capacity, limiting their P-removal capacity.
Exercise 7.4.1 | Exercise 7.4.1 a | Briefly describe the following aspects of the biological sulphate reduction (BSR) process: Sulphate-reducing pathways. | In both natural and engineered systems, biological sulphur conversion can be classified into two categories, i.e. 'assimilatory sulphate reduction' and 'dissimilatory sulphate reduction (DSR)' pathways, for the purpose of synthesizing sulphur-containing molecules and cellular energy production, respectively. The main reactions associated with DSR pathways are closely related to the sulphur and carbon cycles and play a crucial role for wastewater organics degradation in the sulphur reduction/SANI process.
Exercise 7.4.1 | Exercise 7.4.1 b | Briefly describe the following aspects of the biological sulphate reduction (BSR) process: The key microorganisms driving sulphate reduction. | Sulphate-reducing bacteria (SRB) and sulphate-reducing archaea (SRA), generally called SRB, can perform respiration with oxidized sulphur compounds in their energy metabolism. To date, more than 120 species and 40 genera belonging to four bacterial classes and two archaeal classes have been documented.
Exercise 7.4.1 | Exercise 7.4.1 c | Briefly describe the following aspects of the biological sulphate reduction (BSR) process: The electron donors for the sulphate-reducing bioprocess. | According to the type of SRB growth (autotrophic or heterotrophic), the different electron donors of SRB reactions are inorganic substrates (H2 and CO) and organic substrates. For more details on SRB reduction rates, related reactions and benefits/drawbacks. It should be noted that, stoichiometrically, 0.67 mol of COD is needed for the complete reduction of 1 mol sulphate.
Exercise 7.4.1 | Exercise 7.4.1 d1 | Briefly describe the following aspects of the biological sulphate reduction (BSR) process: Applications of the BSR process. | SRB-based technologies can be applied in different types of wastewater treatment, such as the removal and reuse of sulphur compounds from sulphur-laden wastewaters (e.g. leather tanning, kraft pulping and food processing), and for flue-gas desulphurization wastewater as well as domestic wastewater with sufficient sulphate compounds contained/added.
Exercise 7.4.1 | Exercise 7.4.1 d2 | Briefly describe the following aspects of the biological sulphate reduction (BSR) process: Influencing factors. | SRB-based applications are significantly affected by temperature, pH, sulphide concentration and COD/SO4 2- mass ratio. It should be also noted that there are different dominant kinetic principles in different SRB applications.
Exercise 7.4.6 | Exercise 7.4.6 a | Briefly describe the following aspects of the SdAD process: The advantages of SdAD. | Compared with the conventional heterotrophic denitrification process, the SdAD process does not require an exogenous organic carbon source, it eliminates problems associated with residual organics, and it produces much less biomass.
Exercise 7.4.6 | Exercise 7.4.6 b | Briefly describe the following aspects of the SdAD process: The electron donor and acceptor of SdAD. | In SdAD, sulphur-oxidizing bacteria utilize the reduced sulphur compounds (mainly sulphide, thiosulphate and elemental sulphur) as electron donors to reduce nitrogen oxides (mainly nitrate, nitrite, nitrous oxide, and nitric oxide) as electron acceptor(s). The end products are commonly sulphate and dinitrogen gas, while the intermediates (mainly NO2¯, N2O, and S0 bio) can also be produced due to the influent sulphur-to-nitrogen ratio.
Exercise 7.4.6 | Exercise 7.4.6 d | Briefly describe the following aspects of the SdAD process: Microorganisms involved with SdAD. | Microorganisms involved in the SdAD process are phylogenetically diverse and mainly consist of sulphur-oxidizing bacteria (SOB) and nitrate-reducing bacteria.
Exercise 7.4.6 | Exercise 7.4.6 e | Briefly describe the following aspects of the SdAD process: Factors affecting the SdAD process. | The reaction rates of SdAD processes are affected by the following factors: 1) the types of sulphur substrates (total dissolved sulphide (TDSd), S0 and S2O32¯) and nitrogen oxides (NO3¯, NO2¯, N2O, NO); 2) the mass ratio of sulphur-to-nitrogen (1.4 gS/gN theoretically) and alkalinity-to-removed nitrogen (maintained at a minimum of at least 4.0-4.6 gCaCO3/gN); and 3) operational parameters including pH (6-8), DO concentration (0.1-0.3 gO2/m3) and temperatures.
Exercise 7.4.10 | Exercise 7.4.10 | Briefly describe sulphur-based resource recovery technologies. | a. Sulphur-based technologies should be considered as an emerging solution for transitioning from passive wastewater treatment to carbon-/energy-neutral treatment with concomitant resource recovery. b. Selective metabolic products and/or intermediates of the sulphate-reducing process, such as biohydrogen (H2), hydrocarbons and poly-hydroxy-alkanoates (PHA) are valuable and recoverable resources. c. Elemental sulphur is also worth recovering and reusing with the assistance of a group of sulphur conversion-based bacteria, namely chemolithotrophic SOB. SOB can use O2/NOx as the electron acceptor to oxidize sulphide to elemental sulphur for resource recovery. This sulphur recovery technology (such as THIOPAQ®) has been successfully applied in industrial wastewater and off-gas treatment. A kinetic model for elemental sulphur production via sulphide oxidation can be developed by using a similar kinetic model for the SdAD process. d. In addition, sulphide is the product of sulphate reduction mediated by SRB, which can extracellularly bound to or precipitate with metal ions in solution, which can be applied for valuable metal sulphide (MeS) recovery (see Table 7.16 in Chen et al., 2020 for examples of MeS compounds). There are two strategies when SRB are applied in metal sulphide production: 1) the metal reacts directly with the sulphide in the sulphidogenic (in-line) system and 2) sulphide is produced and separated as a metal precipitation agent (in the offline system). This (biogenic-)metal sulphide recovery system can be designed based on the following design examples.
Exercise 8.4.5 | Exercise 8.4.5 a | Hypochlorous acid (HOCl) and peracetic acid (CH3COOOH) are both weak acids that function as disinfectants. For both compounds, the neutral (acid) form is far more effective as a disinfectant than its conjugate base. For temperature conditions that are commonly applied in municipal wastewater disinfection, representative values of pKa for HOCl and CH3COOOH are 7.5 and 8.1, respectively. Given this information: Comment on the efficacy of these compounds at pH values above and below their respective pKa values. In other words, would you expect them to function better at pH above the pKa value or at pH below the pKa value. Justify your answer. | When the pH is below the pKa of an acid, the protonated form will be present at relatively high concentration. The farther the pH is depressed below the pKa, the larger the fraction of the protonated form. In the case of HOCl and PAA, the protonated forms are the most effective disinfectants. Therefore, both compounds will function better as disinfectants when they are present in solution at pH below their respective pKa values.
Exercise 8.4.5 | Exercise 8.4.5 b | Hypochlorous acid (HOCl) and peracetic acid (CH3COOOH) are both weak acids that function as disinfectants. For both compounds, the neutral (acid) form is far more effective as a disinfectant than its conjugate base. For temperature conditions that are commonly applied in municipal wastewater disinfection, representative values of pKa for HOCl and CH3COOOH are 7.5 and 8.1, respectively. Given this information: Discharge permit limitations for municipal wastewaters often require that treated wastewater have a pH between 6-9; typical effluent pH is often in the vicinity of 7.5. Comment on the relative efficacy of free chlorine and PAA at low, medium, and high values of effluent pH (i.e. pH = 6, pH = 7.5, and pH = 9). | At low pH (i.e. pH = 6), both compounds will be present (largely) in their respective protonated forms. Therefore, HOCl and PAA are both likely to be relatively effective at this pH value. At medium pH (i.e. pH = 7.5) HOCl will be roughly evenly split between HOCl and its conjugate acid, OCl¯. PAA will also be present as a mixture of its neutral (protonated) form and its conjugate acid, but a larger fraction of PAA will exist in solution as its protonated form than HOCl. In other words, it is likely that PAA will be less affected by this pH condition than HOCl. At high pH (i.e. pH = 9), both compounds will be dominated by their deprotonated forms (i.e. their conjugate bases, both of which are anions). As such, the performance of both compounds will be adversely affected by this pH condition, relative to lower pH conditions. However, since the pKa of PAA is roughly 0.6 pH units higher than that of HOCl, it is likely that PAA will be less adversely affected by this relatively high pH condition than will HOCl.
Exercise 9.4.1 | Exercise 9.4.1 | What is the required pressure to guarantee air discharge during operations when designing blower sizing? | To guarantee that the air is released, the discharge pressure of the blower (pdisch, relative to atmospheric pressure) must exceed the pressure requirements of the system, consisting of the sum of the pressure losses in the system: pdisch ≥ ρ·g·Z + hL + DWP(AFR) The pressure losses on the right-hand side of are the following: • the hydrostatic head loss ρ·g·Z due to the diffuser submergence Z; • the head loss of the air distribution line (friction head hL), which for practical purposes may be considered independent of the airflow rate; • the dynamic wet pressure (DWP), i.e., the diffuser head loss, which is a function of the airflow rate (AFR) and needs to be provided by the manufacturer.
Exercise 9.4.2 | Exercise 9.4.2 | What happens when the pressure requirements approach the maximum discharge pressure of the blowers? | When the pressure requirements approach the maximum discharge pressure of the blowers, the blowers begin to surge. The surge zone is an area of operation and must be avoided because the vibrations that the blowers are subject to may cause structural failure. An automated system shuts down the blowers when the search begins.
Exercise 9.4.3 | Exercise 9.4.3 | Explain what diffuser flexing is. | Diffuser flexing, also known as purging, is the practice of inflating membrane diffusers by feeding airflow higher than the usual maximum range (e.g., 130-150 % of maximum operating airflow), in order to dilate the pores of the membrane diffusers and therefore delay the occurrence of fouling.
Exercise 9.4.4 | Exercise 9.4.4 | What is the difference between the oxygen transfer rate (OTR) and the standard oxygen transfer rate (SOTR) if the test is conducted at 15 °C and 700m AMSL (i.e., height above mean sea level)? | The OTR is calculated from the dissolved oxygen time series of reiteration in field conditions. In this case field conditions are 15 °C and 700 m above sea level. The standardized OTR, SOTR, is the value corrected for 20 °C and 1 atm. For more information on this procedure.
Exercise 9.4.5 | Exercise 9.4.5 | What happens to the kLa if we use excessively slow DO sensors? | Using excessively slow DO sensors causes a delay between the actual dissolved oxygen and the reading of that value by the sensor. The delay is very visible at the beginning of the re-aeration process, i.e., when the slope of the re-aeration curve (DO vs. time) is very high and any error on the horizontal axis corresponds to large errors on the vertical axis. This can be visibly observed because the fitting curve, which is an ideal exponential, will differ from the experimental data, which will be more of a sigmoid. At the end of re- aeration, when the curve is almost horizontal because it is approaching the asymptote (DO saturation), the speed of the DO sensor is immaterial. Hence, a slow DO sensor results in underestimation of kLa.
Exercise 9.4.6 | Exercise 9.4.6 | Can we use plant effluent to perform a clean water test in order to determine the kLa? | No, we cannot, because plant effluent still contains residual organics that would alter the result and produce lower kLa than tap water.
Exercise 9.4.7 | Exercise 9.4.7 a | What are the main types of aerators? | There are two main types of aeration technologies: the first is surface aeration and the second is submerged aeration.
Exercise 9.4.7 | Exercise 9.4.7 b | What are the main differences between main types of aerators? | There are two main types of aeration technologies: the first is surface aeration and the second is submerged aeration. Surface aeration is mechanical and relies on impellers. Subtypes: High-speed versus low-speed surface aerators, with horizontal or vertical shafts. Submerged aeration relies on bubbles released throughout the floor by coarse-bubble or fine-bubble diffusers, or by mechanical devices (turbines or jets). Subtypes: Coarse-bubble versus fine-bubble aeration systems.
Exercise 9.4.8 | Exercise 9.4.8 | If cleaning of aeration system is not an option at a given wastewater treatment plant, what are the challenges that the operators will face? | When cleaning is not practised or not possible, fine-pore diffusers foul and the pressure drop of these diffusers increases. At the same time, the diffusers experience a decline in performance, measured as αFSOTE so αF decreases over time. The consequence is an increase in the requirements for airflow, blower energy and pressure, with potential blower failure if pressure requirements become excessive. Cleaning is always recommended but when it cannot be practised, technologies immune from fouling, such as coarse-bubble diffusers or mechanical aeration systems, are recommended.
Exercise 9.4.9 | Exercise 9.4.9 | What is the cleaning frequency for fine-pore diffusers? | Experience and documented measurements in the field suggest that the diffusers should be cleaned at least once every 24 months, and preferably once a year.
Exercise 9.4.10 | Exercise 9.4.10 | Define aeration efficiency. | The aeration efficiency (AE, expressed in kgO2/kWh) is defined by the oxygen transfer rate OTR (in kg/h) relative to the power P (in kW) drawn by the aeration system: AE = OTR/P. The AE is a measure for the efficiency of the aeration system, in contrast to the OTR, which only defines the capacity of the aeration system.
Exercise 9.4.11 | Exercise 9.4.11 | With regard to the effect of process design on aeration efficiency, briefly describe two favourable design criteria or configurations useful for improving the aeration efficiency in wastewater treatment plants. | The aeration efficiency in wastewater treatment plants can be improved by the following design measures: Use of anoxic or anaerobic selectors: they result in improved (higher) alpha factors, probably by uptake of soluble contaminants (surfactants) into the biomass. Relatively high sludge retention time (SRT): higher SRT systems, which operate with higher biomass concentrations, remove or sorb the surfactants early in the process, improving the average oxygen transfer efficiency and outweighing the increasing oxygen requirement for increasing SRT.
Exercise 9.4.12 | Exercise 9.4.12 | With regard to the effect of process operation on aeration efficiency, describe three operating factors that adversely affect (reduce or deteriorate) the aeration efficiency in wastewater treatment plants. | Type of aerators used: fine-pore diffusers are the most efficient, coarse bubble diffusers are much less efficient; surface aerators are also less efficient. Fouling: the oxygen transfer efficiency of fine-pore diffusers decreases over time. Cleaning fine-pore diffusers is almost always required and restores process efficiency and reduces power costs. Other aerator types are less prone to fouling. Surfactants: surface active agents accumulate at the air-water interface of rising bubbles, increasing the rigidity of the interface and reducing internal gas circulation and overall transfer rate.
Exercise 9.4.13 | Exercise 9.4.13 | What is the process performance for an aeration system operating at constant airflow and variable process loading (hence, variable DO)? | An aeration system operating a constant airflow will over-deliver air when process loading is below average and under-deliver air when the process loading is above average. Although the power demand and energy requirement for this aeration system is constant because the airflow is constant, the process performs poorly at peak loading (i.e., when it is most needed) and excessively well at minimum loading. This is not the correct way to operate a process and should be avoided
Exercise 10.4.2 | Exercise 10.4.2 a | Explain what bulking sludge is. | Bulking sludge' refers to the excessive growth of filamentous bacteria in an activated sludge process, to such an extent that suspended solids cannot be maintained in the settler. Indeed, filamentous bacteria result in open and porous sludge flocs, which experience hindered settling.
Exercise 10.4.2 | Exercise 10.4.2 b | Explain the bulking sludge's consequences for process performance. | Bulking sludge is an operational or empirical problem, there is not an exact scientific index to distinguish bulking sludge from non-bulking sludge. The volume fraction of filamentous bacteria in the activated sludge community which causes settling problems could be minor. Volume fractions of 1-20% are sufficient to cause bulking sludge.
Exercise 10.4.3 | Exercise 10.4.3 | To what extent is bulking sludge related to the SVI? | In practice, bulking sludge is associated with a high SVI. However, there is no generally accepted 'critical value' above which bulking sludge occurs, i.e. in the sense that it causes settler failure. In the Netherlands for instance, an SVI above 120 ml/g is already considered bulking sludge.
Exercise 10.4.4 | Exercise 10.4.4 a | Describe the diffusion-based selection theory to explain the occurrence of bulking sludge. | Diffusion-based selection theory. Filamentous bacteria can easily grow outside the flocs, which means that the filamentous bacteria observe a higher substrate concentration than the floc-formers inside the floc. As a result, diffusion-dominated conditions (i.e., low substrate concentrations) typically result in the growth of open, filamentous structures.
Exercise 10.4.4 | Exercise 10.4.4 b | Describe the kinetic selection theory to explain the occurrence of bulking sludge. | Kinetic selection theory. This theory regards filamentous microorganisms as K strategists, i.e., characterized by a higher affinity (lower affinity constant KS) and a lower maximum growth rate than floc-forming bacteria, the latter being r strategists. In systems where the substrate concentration is low (typically CS < KS), as in continuously-fed completely mixed systems, filamentous bacteria have a higher specific growth rate than floc-forming bacteria, and thereby win the competition for substrate. In systems where the substrate concentration is high, as in plug-flow reactors and sequencing batch reactor (SBR) systems, floc-forming bacteria will dominate.
Exercise 10.4.4 | Exercise 10.4.4 c | Discuss how the diffusion-based selection theory and the kinetic selection theory relate to each other when explaining the occurrence of bulking sludge. | Relation between diffusion-based selection theory and kinetic selection theory. KS is typically used in activated sludge processes as an apparent mass transfer parameter, lumping substrate affinity and diffusion resistance. As such, the kinetic selection theory and the diffusion-based selection theory effectively both describe growth limited by diffusion at low substrate concentration. Indeed, the lower mass transfer resistance experienced by filamentous bacteria will translate into a lower KS, classifying them as K strategists.
Exercise 10.4.5 | Exercise 10.4.5 | Explain the storage selection theory. | Microorganisms generally store substrate under high substrate concentrations, certainly when they undergo feast/famine conditions as usually occurs in a wastewater treatment plants. Non-filamentous (floc-forming) microorganisms are traditionally supposed to have a higher storage ability than filamentous ones. The storage ability gives them a competitive advantage in highly dynamic activated sludge systems such as plug-flow reactors, SBR and selector systems. Even though storage and regeneration may not be prime selection factors against filamentous bacteria, they do play a key role in selector-like systems because the high loading conditions and plug-flow conditions to prevent diffusion limitations also induce the storage response by the floc-forming bacteria. The prime selection factors for filamentous bacteria causing bulking sludge are generally accepted to be diffusion-based and/or kinetic selection.
Exercise 10.4.6 | Exercise 10.4.6 a1 | What are the main non-specific methods to control bulking sludge? | Non-specific methods comprise the use of oxidants to destroy filamentous bacteria causing bulking sludge. Examples are chlorination, ozonation and the application of hydrogen peroxide.
Exercise 10.4.6 | Exercise 10.4.6 b | What drawbacks do the main non-specific methods to control bulking sludge have? | (i) non-specific methods do not remove the causes for the excessive growth of filamentous microorganisms and their effect is therefore only transient; (ii) when using oxidants, there are environmental and ecotoxicological concerns about the potential formation of undesirable by-products such as halogenated organic components, and (iii) other micro-organisms could also be affected by the oxidants, given that this method is non-specific. If slow-growing bacteria such as nitrifiers were to be affected, they would take a long time to recover, resulting in a suboptimal effluent quality.
Exercise 10.4.7 | Exercise 10.4.7 a | Describe the principle of specific methods to control bulking sludge. | Specific methods are preventive methods which favour the growth of floc-forming bacteria at the expense of filamentous bacterial structures.
Exercise 10.4.7 | Exercise 10.4.7 b | What is the principle behind the methods control bulking sludge? | Finding the right environmental conditions to achieve this is a challenge in activated sludge plants, but when successful, it enables the permanent control of bulking sludge.
Exercise 10.4.7 | Exercise 10.4.7 c | How are the methods to control bulking sludge established in practice? | Preventive actions are based on the idea that the substrate conversion should not be limited by diffusion. This requires that readily biodegradable substrates are consumed at high substrate concentrations, such that the substrate uptake rate is close to its maximum value (at least qs/qsmax > 0.6 and preferably qs/qsmax > 0.8). In addition, the oxygen concentration should also be non-limiting (typically O2>1 mg/l), at least during the period where readily biodegradable substrate is available. This is largely ensured by a properly designed plug flow or compartmentalized selector tank.
Exercise 10.4.8 | Exercise 10.4.8 | Explain the principle of selectors to control bulking sludge. | In order to ensure that substrate conversion is not limited by diffusion and thus prevent bulking sludge, a high uptake rate and (almost) complete removal of readily biodegradable organics should be established in the entrance part of the activated sludge process. This initial part of the biological reactor, characterized by a plug- flow hydraulics (i.e., a low dispersion number) and by an adequate macro-gradient of substrate, is termed the selector. The selector can also be a small initial zone of the reactor which receives the influent and sludge return flows, as long as it leads to a high uptake rate and almost complete removal of readily biodegradable organics.
Exercise 10.4.9 | Exercise 10.4.9 | Discuss the implementation of selectors through their main design parameters to control bulking sludge. | • Selectors need to consist of at least three compartments to ensure sufficient plug-flow behaviour. • Selectors can be aerobic, but also anoxic or anaerobic. In an aerobic selector, the oxygen concentration should be sufficiently high (O2 > 2mg/l) as verified with an oxygen sensor in the first compartment. The entrance of oxygen into anoxic or anaerobic selectors needs to be avoided at all times. A low DO in the selector leads to oxygen gradients and growth of filamentous bacteria (low DO bulking). • The sludge loading rate (SLR, kgCOD/kgTSS.d) needs to be kept close to a prescribed value1 , which depends on the selector type (higher SLR for aerobic than for anoxic selectors, not specified for an anaerobic one) and decreases along the selector path (highest SLR in the first selector compartment). The SLR needs to be high enough to avoid substrate limitation and low enough to enable full conversion of readily biodegradable substrate. • The contact time needs to be kept within a certain prescribed range1 , which depends on the selector type (increases for aerobic ≥ anoxic ≥ anaerobic), load, temperature and influent readily biodegradable COD fraction. The contact time needs to be sufficiently long to ensure complete conversion of readily biodegradable substrate. On the other hand, too long contact times may result in a too low concentration of substrate, favouring the growth of filamentous microorganisms. • For an aerobic selector, the floc loading (in kgCOD/kgTSS) needs to be in a certain range1 . • The design of an anoxic selector is primarily based on the ratio of readily biodegradable organics to nitrate (RBCOD / NO3 - -N), which needs to be higher than the typical value for direct denitrification, taking into account that an important fraction of readily biodegradable COD is converted into storage products. Nitrate needs to be in surplus in the anoxic reactor, even though periods with temporarily anaerobic conditions are not harmful. • For anaerobic selector design, the ratio of readily biodegradable COD (VFA and fermentable COD) to phosphate needs to be kept within a certain range to make sure that hardly any readily biodegradable COD enters the main aeration basin. • For anaerobic selector design, the main criterion is that readily biodegradable COD (VFA and fermentable COD) is fully converted under anaerobic conditions. • Mixing conditions in anoxic and anaerobic conditions are not critical. Also, carry-over of readily biodegradable organics into the aerated stage is much less detrimental than in aerobic conditions. This is based on the experimental work by Martins (2004).
Exercise 10.4.10 | Exercise 10.4.10 | Describe how aerobic granular sludge relates to bulking sludge. | Aerobic granular sludge is the opposite phenomenon to bulking sludge. Granular sludge is formed when substrate conversion is not limited by diffusion. For aerobic granules to be formed, the removal of readily biodegradable organics should take place with minimal substrate gradients over the sludge floc or under fully anaerobic conditions. Anaerobic selectors are particularly suitable to promote aerobic granular sludge formation since they select phosphate and glycogen accumulating bacteria (PAO and GAO), given that ordinary heterotrophic filamentous bacteria are unable to grow under anaerobic conditions. The relatively low maximum growth rates of PAO and GAO result in lower substrate and oxygen uptake rates, which means that substrate/oxygen uptake rather than diffusion is the rate-limiting-step. Moreover, diffusion limitation is minimized since growth takes place on substrate stored within the cell.
Exercise 11.4.1 | Exercise 11.4.1 a | What are the main differences concerning reactor configuration between an aerobic granular sludge (batch) system and a conventional (continuous) activated sludge system? | Main differences concerning reactor configuration between an aerobic granular sludge (batch) system and a conventional (continuous) activated sludge system: • In contrast to conventional activated sludge systems, AGS systems are either built as minimum three AGS reactors in parallel, or as one or more AGS reactors (usually two) and a buffer tank. Indeed, the batch-wise operation implies that a single reactor cannot receive influent all the time, since influent cannot be fed during the reaction or settling phase. A minimum of three AGS reactors in parallel is required for continuous operation. Alternatively, it is possible to opt to build a buffer tank and as such reduce the number of AGS reactors. The latter may be more economical for smaller plants (requiring a low reaction volume) as well as for larger plants that would require more than three reactors (and where a buffer tank enables a shorter feeding phase with higher flows, and thus a relatively longer reaction time). Note that for large facilities, activated sludge processes are also designed with parallel reactors. • Another main difference is that an AGS reactor is always fed in plug-flow mode. The plug-flow regime allows simultaneous feeding and discharge.
Exercise 11.4.1 | Exercise 11.4.1 b | What are the main differences between traditional sequencing batch processes and aerobic granular sludge (batch) systems? | Main differences between traditional sequencing batch processes and aerobic granular sludge (batch) systems: • The feeding in AGS is from the bottom in a plug flow through the reactor. Therefore, the reactor has a constant volume and there is no need for a mechanical decanter for effluent extraction, nor for decanting time within the cycle length. The plug-flow feeding also eliminates the need for a mixer during the anaerobic phase, since the influent is in contact with the granules from the moment it enters the reactor. • Due to the fast settling, there is virtually no cycle time required for sludge settling; only a short time to eliminate turbulence after the aeration phase is required.
Exercise 11.4.2 | Exercise 11.4.2 | What are the main advantages of an aerobic granular sludge (batch) system compared to a conventional (continuous) activated sludge system? | An aerobic granular sludge batch reactor compared to a continuous activated sludge plant: • Has a smaller footprint: no need for settling tanks and the AGS reactor is designed to be more compact, because of high biomass concentrations allowing a high volumetric loading rate (Pronk et al., 2015a). • Needs fewer construction materials, for the same reasons. • Needs less mechanical equipment, such as recycle pumps, return sludge pumps, clarifier bridges, mixers. This saves on investment, maintenance requirements and energy usage (Pronk et al., 2015a). • Reaches a high effluent quality more easily: batch-wise operation ensures a relatively high substrate concentration compared to completely mixed reactors, thus minimizing diffusion limitation and therefore allowing higher conversion rates. Also, the reactor content is not continuously fed with wastewater, resulting in a faster drop in concentration in the liquid phase of the reactor. Lastly, the N removal is not dependent on an internal recycle flow from the aeration tank to the pre-denitrification tank1 , but can be controlled by the oxygen set-point and length of the post-denitrification phase.
Exercise 11.4.3 | Exercise 11.4.3 a | Which four unit operations of an activated sludge plant can be compared to the processes in a single aerobic granular sludge tank? | The anaerobic, aerobic, anoxic, and settling tank.
Exercise 11.4.3 | Exercise 11.4.3 b | How is it possible that all four processes (the anaerobic, aerobic, anoxic, and settling tank)can be performed in one reactor in aerobic granular sludge tank? | The large size of granules compared to activated sludge flocs enables different redox zones (from outside to core: aerobic, anoxic, and (with large granules) anaerobic) in each granule, favouring bacterial communities with different functions (organic carbon removal, phosphorus removal, nitrification, and denitrification). The anaerobic plug-flow feeding through the settled bed followed by the aeration and post- denitrification phase enables biological phosphate removal. The high settling velocity of the granules enables the integration of the settling in the reactor. Moreover, batch scheduling makes it possible to adapt the phases within the cycles as well as the cycle length to reach the desired effluent quality (e.g., by applying a separate denitrification phase to complement simultaneous nitrification-denitrification).
Exercise 11.4.4 | Exercise 11.4.4 a | What are the advantages of including a primary settling tank in conventional activated sludge systems and to a lesser extent in AGS systems? | A primary settling tank for conventional activated sludge is advantageous to decrease the load on the biological reactor and the associated oxygen consumption by removing suspended solids. Moreover, primary sludge has a very good biogas production potential and is therefore advantageous in view of energy recovery. In an AGS system, suspended solids are removed via the sludge selection spill during settling so there is not a real need for a primary settler for suspended solids removal. Also, the total AGS excess sludge (consisting of the floc fraction with suspended solids on the one hand and granules on the other hand) has a similar biogas production potential as the combined primary and secondary sludge for activated sludge tanks.
Exercise 11.4.4 | Exercise 11.4.4 b | How are suspended solids removed when a primary settling tank is not included in the AGS system design? | The suspended solids will be mainly either removed by uptake by protozoa, metazoa or end up in the flocculated sludge fraction. This is removed as excess sludge during the sludge selection spill during settling in the batch cycle. Colloidal material that will also partly be removed as primary sludge could potentially also be hydrolysed in the anaerobic feeding phase and result in substrate for EBPR. The flocculent fraction has a short solid retention time (SRT) in the process (Ali et al., 2019) and particulates are therefore marginally mineralised in the AGS reactor.
Exercise 11.4.4 | Exercise 11.4.4 c | What are the advantages of avoiding the construction of a primary settling tank? | The advantages of avoiding the construction of a primary settling tank are: a smaller area required for the treatment plant (even though the biological reactor may need to be slightly larger), less odour emission and easier operation.
Exercise 11.4.5 | Exercise 11.4.5 a | What are the main drivers for granulation? | The formation of compact granules is stimulated by: • having high substrate concentrations during feeding and making sure that diffusion is not limiting • selecting slow-growing organisms. • selective pressure due to the difference in settling velocity.
Exercise 11.4.6 | Exercise 11.4.6 a | How does the feast-famine regime contribute to stable granulation? Situate this regime in the SBR cycle. | The feast-famine regime ensures periods with high substrate concentrations in the reactor alternate with periods without substrate supply. This favours slow-growing organisms.
Exercise 11.4.6 | Exercise 11.4.6 b | What happens during the feast-famine regime? Situate this regime in the SBR cycle. | During the feast phase, i.e., the anaerobic feeding phase, there is readily biodegradable BOD (RBCOD) uptake by PAO and GAO and conversion to storage polymers. However, during the famine phase, i.e., the aeration phase, there is consumption of storage polymers by PAO and GAO, since they do not compete on growth rate; they do so at a relatively low specific growth rate.
Exercise 11.4.7 | Exercise 11.4.7 | Why is a continuous stirred tank reactor (CSTR) not preferable for granule formation? | Substrate concentrations in CSTRs are typically very low, leading to low substrate penetration in immobilised biomass such as granular sludge. This induces flocculent biomass growth since this will have less influence from diffusion limitation.
Exercise 11.4.8 | Exercise 11.4.8 | Will fast-growing heterotrophic bacteria be able to develop in the aerobic granular sludge reactor? | No, because the RBCOD concentration in the aerobic phase is almost zero and if they grow, they are removed within 0.5-5.0 d via the sludge selection (or excess sludge) spill.
Exercise 11.4.9 | Exercise 11.4.9 a | Which substrate is suitable for the formation of compact granules? | A suitable substrate for the formation of compact granules is RBCOD.
Exercise 11.4.9 | Exercise 11.4.9 b | How does the take-up rate of RBCOD influence the anaerobic feeding time of a full-scale plant? | Municipal wastewater does not usually contain a lot of RBCOD (≤ 100 g/m3 , depending on the type of sewer system). An anaerobic feeding phase of 1 hour (determined in general more by the hydraulic design than based on biokinetic parameters) is more than sufficient to take up all the RBCOD by the granular sludge. A part of the slowly biodegradable COD can also be anaerobically hydrolysed, fermented and stored during the 1-hour feeding phase.
Exercise 11.4.9 | Exercise 11.4.9 c | Compared with municipal full-scale wastewater, how does the take-up rate of RBCOD influence the anaerobic feeding time with lab-scale reactors and/or industrial wastewater treatment plant? | In lab-scale reactors and/or industrial treatment plants, the anaerobic feeding time could differ according to the anaerobic PHA storage. In these reactors the hydraulic considerations are less dominant and the anaerobic time might be designed according to the anaerobic substrate uptake kinetics.
Exercise 11.4.10 | Exercise 11.4.10 a | Does aerobic granular sludge coagulate under reduced shear stress? | No, the granule has a stable structure and does not coagulate under reduced hydrodynamic shear.
Exercise 11.4.10 | Exercise 11.4.10 b | In aerobic granular sludge, is shear an important granular selection prerequisite? | With the selection for PAO and GAO during the anaerobic feed, shear is not an important granular selection prerequisite.
Exercise 11.4.11 | Exercise 11.4.11 | What is the difference between sludge selection spill and excess granular sludge? | The sludge selection spill mainly consists of the flocculent fraction and is discharged during settling to establish a hydraulic selection pressure for the sludge that is not settling well (Pronk et al., 2015a). The excess granular sludge is granules that are discharged in order to maintain a constant biomass concentration in the reactor and also to remove large granules that consist of a significant inactive volume fraction. Both these discharges differ in concentration, morphology and SRT of the sludge.
Exercise 11.4.17 | Exercise 11.4.17 | Why is the COD, N and P concentration in the effluent of an AGS system usually low enough to be discharged without post-treatment? | In a continuous reactor the concentrations are always low, thus giving conversion close to the KS value for the substrate, i.e., reaction rates are reduced. In a batch operation the concentrations are initially high resulting in high conversion rats. Moreover, in a continuous reactor there is continuous input of pollutants making it more difficult to reach very low values. In addition, the cycle time and different phase lengths can be adapted to reach the optimal effluent quality.
Exercise 11.4.19 | Exercise 11.4.19 | Is there a need for external dosage of organic carbon during post-denitrification in AGS? | External carbon dosage is not required because during the anaerobic feeding there is storage of PHA throughout the granule. During aeration, only the PHA in the outer layer is oxidised with O2. Inside the granule the PHA is already used for denitrification during the aerobic phase. During the post-denitrification phase PHA is used in the entire granule. This is in contrast to activated sludge, where the entire floc is aerobic during aeration and many more storage polymers are oxidised with O2.
Exercise 11.4.20 | Exercise 11.4.20 a | One peculiarity of the PAOs is the production of PHA and the capacity of PO4 3- uptake. From literature, it is usually found that PAO can accumulate up to 0.30 gP/gVSS, while in normal organism P uptake is usually around 0.02 gP/gVSS. The growth yield of both ordinary heterotrophs, as well as phosphate accumulating organisms averages 0.4 kgVSS/kgCODconsumed. Why is the phosphate uptake higher than the phosphate release? | Due to the net biomass growth (which is determined by the biomass yield.
Exercise 11.4.20 | Exercise 11.4.20 b | One peculiarity of the PAOs is the production of PHA and the capacity of PO4 3- uptake. From literature, it is usually found that PAO can accumulate up to 0.30 gP/gVSS, while in normal organism P uptake is usually around 0.02 gP/gVSS. The growth yield of both ordinary heterotrophs, as well as phosphate accumulating organisms averages 0.4 kgVSS/kgCODconsumed. What causes nett P removal in an AGS system? | Nett P removal is obtained by wasting the excess of biomass accumulating P.
Exercise 11.4.20 | Exercise 11.4.20 c | One peculiarity of the PAOs is the production of PHA and the capacity of PO4 3- uptake. From literature, it is usually found that PAO can accumulate up to 0.30 gP/gVSS, while in normal organism P uptake is usually around 0.02 gP/gVSS. The growth yield of both ordinary heterotrophs, as well as phosphate accumulating organisms averages 0.4 kgVSS/kgCODconsumed. Why is PO4 3- uptake competing with the oxygen consumption of nitrification? | PAO will use oxygen as the electron acceptor to oxidize the storage polymer PHA during the aerobic phase. This creates energy for their anabolism and for the uptake of PO4 3-. Since nitrifiers also need oxygen, both populations compete for it.
Exercise 11.4.22 | Exercise 11.4.22 | What are the two main parameters determining the thickness of the aerobic layer? | 1) Activity of the micro-organisms and dissolved oxygen (DO) concentration. 2) Oxygen is used to oxidize ammonium to nitrate and to oxidise BOD. The aerobic and anoxic layer thickness in the granules will be determined by the amount of oxygen in the bulk and the rate at which it is oxidized at the granule outer layer.
Exercise 11.4.23 | Exercise 11.4.23 a1 | Which conversion process will be affected in the case of an increasing DO? | denitrification will be affected because the anoxic volume is smaller.
Exercise 11.4.23 | Exercise 11.4.23 a2 | What is the effect on the effluent in the case of an increasing DO? | NO3 - will remain in the effluent.
Exercise 11.4.23 | Exercise 11.4.23 b1 | Which conversion process will be affected in the case of a decreasing DO? | nitrification will be affected because the aerobic volume is smaller.
Exercise 11.4.23 | Exercise 11.4.23 b2 | What is the effect on the effluent in the case of a decreasing DO? | More NH4 + in the effluent.
Exercise 11.4.24 | Exercise 11.4.24 | How does the size of the granules influence the ratio of aerobic/anoxic volume of the granules? Complete the following sentence. At the same DO, smaller granules have a relatively ...... aerobic volume and ...... anoxic volume than larger granules. | At the same DO, smaller granules have a relatively higher aerobic volume and lower anoxic volume than larger granules.
Exercise 11.4.26 | Exercise 11.4.26 a | For wastewater process monitoring, why are the measured concentrations low during reactor feeding? | Due to the plug-flow regime during the feeding phase, the instruments (kept at the top of the reactor) still measure the effluent concentration of the previous batch, thereby measuring low values.
Exercise 11.4.26 | Exercise 11.4.26 b1 | For wastewater process monitoring, indicate which measurements are usually automated? | NH4 + , NO3 - , ORP, pH.
Exercise 11.4.26 | Exercise 11.4.26 b2 | For wastewater process monitoring, indicate which measurements are usually manual? | COD, total N, total P.
Exercise 11.4.27 | Exercise 11.4.27 a | What are the different phases in the operation of an aerobic granular sludge lab-scale SBR? | Fill, react, settle, drain, and idle phase.
Exercise 11.4.27 | Exercise 11.4.27 b1 | What is the difference in phases with a full-scale aerobic granular sludge process? | In the full-scale process the filling and draining phase are combined.
Exercise 11.4.27 | Exercise 11.4.27 b2 | What are the consequences of a full-scale aerobic granular sludge process? | In the full-scale process the filling and draining phase are combined, which saves cycle time and complex constructions. Smaller reactors can be built. The full-scale plant works at a constant volume.
Exercise 11.4.27 | Exercise 11.4.27 c | How is the sludge spilled in a lab-scale reactor compared to a full-scale reactor? | In a lab-scale reactor, withdrawal of liquid at around the mid-column level is used as a selection pressure on fast-settling sludge. In full-scale Nereda© plants however, effluent flows out from the top. The hydraulic selection pressure is established via a separate sludge selection spill from the reactor for the poor settling sludge, which is called the sludge selection spill.
Exercise 11.4.28 | Exercise 11.4.28 | What is the critical difference between process control of a continuous versus a batch process? | Both operations try to achieve the desired effluent concentrations. In a continuous process the control is often based on a set-point for the concentration equal to the effluent concentration. In a batch process the control is based on the reaction rate (i.e., the change in concentration over time). The batch operation allows a more flexible operation. A flexible operation can better deal with external conditions, maintaining a high quality of the effluent. The batch operation can change the time schedule based on the influent conditions (flow rate, concentrations), therefore e.g., the time schedule can be shortened during a peak hydraulic load. As in the conventional activated sludge system, there is the necessity to both design and operate the reactors based on the hydraulic and biological conditions.
Exercise 11.4.31 | Exercise 11.4.31 a | The concentration peaks per batch vary over the day. Accordingly, the sludge load also varies over the day; this similarly occurs in the conventional activated sludge process. However, to make sure that the sludge loading per batch stays optimal, the concentration peaks in the batch cycle are controlled by adapting the feeding time. When the influent is transported to the WWTP via a combined sewer, the COD concentration in the influent will decrease significantly during a rain event (assume that the COD of rain is equal to zero). How does the sludge loading rate change? | The sludge loading rate remains more or less constant. The sludge loading rate is defined by the COD concentration multiplied by the flow rate, divided by the amount of biomass in the reactor. The loading rate of the system does not change too much with a rain event (the flow increases but the total COD load reaching the plant will probably be the same). It is assumed here that rainwater is relatively clean, although it might contain street run-off or solids from the sewer.
Exercise 11.4.31 | Exercise 11.4.31 b | The concentration peaks per batch vary over the day. Accordingly, the sludge load also varies over the day; this similarly occurs in the conventional activated sludge process. However, to make sure that the sludge loading per batch stays optimal, the concentration peaks in the batch cycle are controlled by adapting the feeding time. Which possible risks occur for the AGS reactor at non-optimal sludge loading rates? | • More readily biodegradable COD than PAOs and GAOs can take up in a cycle, which reduces selection pressure for PAO and GAO and causes the proliferation of fast-growing heterotrophic bacteria in non-granular shape. • Oxygen demand is higher than oxygenation capacity. • Peak concentrations of NH4-N and oxidisable organic N for which the available mass of nitrifiers cannot oxidise within the available aeration time and thus ammonium concentrations exceed effluent demands. • The presence of specific degradable compounds that may cause substrate inhibition when their concentration is too high (e.g., for industrial wastewater). NOTE: If there are a couple of cycles with non-optimal sludge loading, this will not damage the system straight away but it should not last for weeks.
Exercise 11.4.33 | Exercise 11.4.33 a | Which are the two factors that could hinder the settling of suspended solids and contribute to their presence in the effluent in AGS? | The presence of suspended solids in the effluent is caused either by rising sludge due to the degasification of nitrogen gas during the feed and decant phase (when the stripping phase has not been applied or was insufficient) and/or by wash-out of particles that intrinsically do not settle (i.e., fats and foams in the influent).
Exercise 11.4.33 | Exercise 11.4.33 b | Which three measures can be taken to marginalise the presence of suspended solids in the effluent in AGS? | • Add an N2 stripping phase before the feeding phase. • Install a baffle in front of the effluent discharge gutter that prevents a possible floating layer from entering the effluent discharge. • When effluent demands are very strict, it is possible to add a post-treatment such as sand filtration or membranes.
Exercise 11.4.34 | Exercise 11.4.34 | Which three setups ensure processing of a continuous flow of wastewater in an aerobic granular sludge wastewater treatment plant? | • Minimum of three sequencing batch reactors in parallel with always one reactor in feed and draw mode for 1/3 of the total cycle time. • Buffer tank in front of the sequencing batch reactor (only one batch reactor is sufficient). The influent is stored when the reactor(s) is/are in the aeration or settling phase. • Combination of a conventional activated sludge system and AGS reactor in parallel where the influent flow is divided over the two systems.
Exercise 11.4.35 | Exercise 11.4.35 | Why can the AGS reactor be designed smaller when a buffer tank is applied? | The AGS reactor can always be fed closer to the maximum VER or loading rate. The buffer tank levels the hydraulic peaks (e.g., hydraulic regulation of daily peaks, wet weather flow).
Exercise 11.4.37 | Exercise 11.4.37 | What are the parameters influencing the hydraulic restrains to design the reactor volumes, assuming a fixed dry weather flow? | • The peak dry weather flow: this is the largest flow corresponding with the maximum reaction time (because the concentrations will be the highest). • The length of the feed and draw phase. • The volume exchange ratio (max. 0.65). o These three parameters will influence the hydraulic restraints to design the total reactor volume (m3 ). • The peak dry weather flow. • The upflow velocity (max. 5m/h) o These two parameters will influence the hydraulic restraints to design the reactor area (m2 )
Exercise 11.4.38 | Exercise 11.4.38 | How can excess granular sludge be applied today and/or in the (near) future? | For agricultural reuse (if legally allowed), energy recovery, inoculation of new treatment plants, resource recovery of Extracellular polysaccharides (EPS) (KaumeraTM).
Exercise 11.4.39 | Exercise 11.4.39 | Which sludge type has the highest methane potential (in m3 CH4/gVSS)? Put the following in order from high to low: primary sludge, activated sludge, aerobic granules, selection spill. | Primary sludge > Selection spill > Activated sludge > Aerobic granules.
Exercise 12.4.1 | Exercise 12.4.1 | List the functions of a secondary settler tank. | Secondary settling tanks have three distinct functions: • clarification, providing a clear effluent with suspended solids removal up to 99.9 %, • thickening of sludge, in the blanket, to provide a concentrated recycle stream and thus lower the RAS flow, • sludge storage, usually on a temporary basis, to cope with overload events.
Exercise 12.4.2 | Exercise 12.4.2 a | List the three main types of (gravitational) final settlers. | The three main different types of (gravitational) final settlers are: • circular clarifiers with a radial flow pattern, • rectangular clarifier with a horizontal flow pattern, • deep clarifiers with a vertical flow pattern.
Exercise 12.4.2 | Exercise 12.4.2 b | What are the typical add-ons to improve the performance of main types of (gravitational) final settlers? | Their operation can be improved by: • a flocculation well, reducing the effluent solids concentration by promoting flocculation, • scum baffles or other scum removal mechanisms, • baffles for flow diversion and energy dissipation, • lamellae, i.e., slanted tubular or plate structures, to reduce the settling time.
Exercise 12.4.3 | Exercise 12.4.3 | Which considerations determine the settler type selection? | The settler type selection is determined by the available space, cost limitation, plant loading, and performance.
Exercise 12.4.4 | Exercise 12.4.4 | What kind of operational problems can occur with inadequate settler implementation (design and/or operation)? | The following are typical operational problems with final settlers: • Shallow tanks (less than 2.5-3 m side water depth) are susceptible to solids overload, leading to scouring (loss of solids) from the sludge blanket or gross clarifier failure due to the sludge blanket reaching the effluent weirs. Maintaining a low sludge blanket level via higher recycle rates (RAS) is therefore important in shallow clarifiers. • Uneven flow distribution between parallel clarifiers can cause overload in some final settlers. • Incorrectly levelled weirs result in uneven weir loading, thus creating local upwelling from the blanket. • Wind exposure can affect the flow circulation pattern and result in uneven weir loading. • Sudden temperature change may cause an unexpected layer inversion, resulting in flotation of the sludge blanket. Freezing in cold climates may cause ice build-up. • Recycle problems caused by suction pipe design. • Algae on weirs can result in uneven weir load. • Anaerobic clumps, which are floating due to methane gas generation, resulting from misaligned sludge removal. • Birds can add extra nutrient load to the effluent. • Bulking sludge, due to bad sludge settling properties (filaments). • Rising sludge, due to nitrogen gas bubbles produced by denitrification in the clarifier.
Exercise 12.4.5 | Exercise 12.4.5 a | What is the purpose of SVI tests? | The Sludge Volume Index (SVI) is a common measure for the settleability of sludge. It describes the volume of 1 g sludge (MLSS) after 30 minutes of settling. It is measured by taking 1 litre of sludge sample in a graduated cylinder, and after initial mixing, leaving it to settle for 30 minutes, after which the sludge volume is read.
Exercise 12.4.5 | Exercise 12.4.5 b | What are typical values of SVI tests? | Well-settling sludge has a typical SVI value of 50 ml/g; an SVI value of 150 ml/g or higher indicates potential filamentous bulking.
Exercise 12.4.5 | Exercise 12.4.5 c1 | What are the main advantage of SVI tests? | The main advantage of the SVI test is that it is easy to perform (simplicity).
Exercise 12.4.5 | Exercise 12.4.5 c2 | What are the main drawback of SVI tests? | The main drawback is that the results may be influenced by the type of sludge and by the MLSS concentration: sludges which settle fast or tests done at lower MLSS concentrations are mostly finished settling in 30 minutes, so the SVI is then an indicator of sludge compactability rather than settleability.
Exercise 12.4.5 | Exercise 12.4.5 d | How can the drawback of SVI tests be overcome? | The results of the SVI test are made more standard by: • diluting the sludge sample so that the settled volume after 30 minutes is 150-250 ml, i.e., diluted SVI test = DSVI test. • diluting the MLSS to a concentration of 3.5 gMLSS/litre and slowly stirring the settling vessel, i.e., stirred SVI test performed at 3.5 gMLSS/litre = SSVI3,5 .
Exercise 12.4.8 | Exercise 12.4.8 | Describe the Vesilind function. | The Vesilind function describes the relation between the zone settling velocity (ZSV) and the MLSS concentration in the tank, reflecting that a higher MLSS results in a lower zone settling velocity hin X s 0 p v ve− ⋅ = ⋅ here vs is the zone settling velocity (m/h), X denotes the MLSS concentration (g/l or kg/m3 ), v0 is the initial settling velocity (m/h), and phin is the hindered settling parameter of the Vesilind function (m3 /kg).
Exercise 12.4.11 | Exercise 12.4.11 a | What is state point analysis (SPA) and what are the associated considerations? | State point analysis is a graphical way of determining the operating conditions of the clarifier, based on its solids mass balances.
Exercise 12.4.11 | Exercise 12.4.11 b | List the variables used to draw the state point diagram, which forms the basis forstate point analysis (SPA). | The SPA method assumes steady-state conditions, it considers only the vertical dimension, it does not take into account compression, and it neglects effluent solids. The state point diagram represents various fluxes in a clarifier (the Y axis) as a function of solids concentration (the X axis). It is based on the gravity (settling) flux, on which the overflow line, the underflow line, and the feed (concentration) line are superimposed.
Exercise 12.4.13 | Exercise 12.4.13 | What is the design principle for final settlers in terms of SHC I and II? | The design principle is to define the clarifier surface area (A) and the recycle ratio (QR) to meet the SHC I and SHC II under any expected MLSS concentration and peak wet weather flow (PWWF) combination. It can be noted that SHC II is only determined by A, while SHC I is influenced by both A and QR. Consequently, SHC II is used to determine the minimum setter area, after which SHC I is applied to determine the minimum recycle ratio.
Exercise 12.4.14 | Exercise 12.4.14 a | What is the Ekama D&O chart? | The Ekama D&O chart reorganizes the information available in the flux theory and the state point diagram.
Exercise 12.4.14 | Exercise 12.4.14 b | How does Ekama D&O chart evaluate the Sludge Handling Criteria SHC I and SHC II? | The Ekama D&O chart plots the overflow rate (the Y axis) against the recycle ratio (the X axis). SHC II is judged based on a straight horizontal line representing the settling velocity at the feed concentration. Above this line, SHC II is not satisfied; the clarifier is overloaded. Below this line, i.e. under under-loaded conditions, SHC I remains to be evaluated. The SHC I line describes the maximum allowable solids flux in terms of the recycle ratio. It defines a series of critical loading conditions related to the minimum flux, which are equivalent to the recycle line being tangential to the gravity flux in the state point diagram (during state point analysis).
Exercise 12.4.15 | Exercise 12.4.15 | Explain the meaning of the criterion boundary line in Ekama D&O chart. | Above a certain recycle ratio (R) it is not possible to determine a critical concentration and minimum solids flux. The criterion boundary line represents the boundary between lower recycle ratios where a critical flux can be found and higher recycle ratios where it cannot be found.
Exercise 12.4.16 | Exercise 12.4.16 | How is the minimum recycle ratio determined based on the Ekama D&O chart? | The minimum recycle ratio can be obtained from the Ekama D&O chart by reading the x value of the chart at the intersection of the SHC II and SHC I lines. For recycle ratios lower than this value, the settler is overloaded because SHC II or both SHC I and SHC II have not been met.
Exercise 13.4.1 | Exercise 13.4.1 a | What are the typical membrane processes driven by pressure? | The membrane processes driven by pressure include microfiltration, ultrafiltration, nanofiltration, and reverse osmosis.
Exercise 13.4.1 | Exercise 13.4.1 b1 | What are the corresponding minimum sizes of matter that microfiltration can reject? | The corresponding minimum size of rejected matter is 0.1 μm.
Exercise 13.4.1 | Exercise 13.4.1 b2 | What are the corresponding minimum sizes of matter that ultrafiltration can reject? | The corresponding minimum sizes of rejected matter are 0.002–0.1 μm.
Exercise 13.4.1 | Exercise 13.4.1 b3 | What are the corresponding minimum sizes of matter that nanofiltration can reject? | The corresponding minimum sizes of rejected matter are ~0.001 μm (100–1,000 Da).
Exercise 13.4.1 | Exercise 13.4.1 b4 | What are the corresponding minimum sizes of matter that reverse osmosis can reject? | The corresponding minimum sizes of rejected matter are < 0.001 μm (solutes).
Exercise 13.4.2 | Exercise 13.4.2 | What is the mechanism of size sieving in membrane separation? | The size-sieving mechanism is a physical process to retain the components that are larger than the membrane pore size, and the smaller components can penetrate through the membrane pores.
Exercise 13.4.3 | Exercise 13.4.3 | Given that a feed liquor contains macro-molecular protein, virus, E. coli, and colloids, can these constituents be removed in a microfiltration (MF) process? | According to size sieving, MF can remove E. coli, while it cannot remove macro-molecular proteins. The removal efficiencies of viruses and colloids depend on their specific sizes. Viruses and colloids larger than 0.1 μm can be removed.
Exercise 13.4.4 | Exercise 13.4.4 a | What are the principal features of MBR technology? | MBR technology has a small footprint, good effluent quality, independent control of SRT and HRT, and small sludge production.
Exercise 13.4.4 | Exercise 13.4.4 b | Which principal features of MBR technology is the most essential? | The most essential feature of MBR technology is the separation of SRT and HRT, which allows the accumulation of activated sludge and furtherly enhanced biological degradation, a reduced footprint, and reduced sludge production. The separation of SRT and HRT relies on the membrane process to retain the activated sludge flocs in the reactor.
Exercise 13.4.5 | Exercise 13.4.5 a | What are the major configurations of MBR? | MBRs mainly have two configurations: side-stream configuration and submerged configuration.
Exercise 13.4.5 | Exercise 13.4.5 b1 | What are merits of sidestream MBR? | With sidestream MBRs it is easy to conduct frequent and/or in situ membrane cleaning and replacement. The configuration can easily be integrated with other activated sludge processes.
Exercise 13.4.5 | Exercise 13.4.5 b2 | What are merits of submerged MBR? | Submerged MBRs are less energy-intensive than side-stream MBRs because the aeration can control membrane fouling by its scouring effects. The configuration can easily be integrated with other activated sludge processes.
Exercise 13.4.5 | Exercise 13.4.5 b | What are shortcomings of sidestream MBR? | Sidestream MBRs usually consume a large amount of energy.
Exercise 13.4.7 | Exercise 13.4.7 | Describe the advantages of the MBR process in removing ordinary pollutants compared with other biological treatment processes. | There are several technical advantages of MBR that make it excellent for ordinary pollutant removal. The membranes can directly reject most sludge flocs, microorganism cells, and suspended solids. This ability to reject is usually enhanced when the membrane pores are narrowed due to adsorption/blocking of foulants or the membrane surface is covered by a dynamic foulant layer, enabling partial rejection of biopolymer clusters and debris, colloidal COD/N/P, and even soluble substances. MF or UF membrane filtration, as a physical process, is not likely to straightforwardly alter the nature of microorganisms. However, it can enhance the biological process due to the high rate of retention of the microorganisms and partial rejection of the pollutants. The complete separation of HRT and SRT enables MBR to maintain a high sludge concentration and a low food-to-microorganism (F/M) ratio (i.e., a lower sludge loading), and to keep the microorganisms in the endogenous respiratory period for more thorough degradation of the pollutants. Also, due to membrane rejection, nitrifying bacteria are normally easier to enrich in the system and more resilient at low temperatures, which is critical for the stable removal of NH4 + -N and beneficial for overall TN removal. However, for biological P removal, MBR is a double-edged sword. On the one hand, MBR can have a high sludge concentration and a high P content per unit mass of sludge (i.e., an overall high P concentration in the sludge phase), and the membrane can reject some of the colloidal P as well; on the other hand, the typically longer SRT (15-30 d) of MBR means a slower discharge of the excess sludge from the system.
Exercise 13.4.8 | Exercise 13.4.8 | Describe the advantages of the MBR process in removing emerging pollutants compared to other biological treatment processes. Which mechanisms do you think are behind its advantageous performance? | For TrOPs which are readily degradable, the removal efficiencies by MBR and CAS are normally comparable, whereas for refractory TrOPs, the MBR is potentially more effective in biological degradation. For TrOPs with strong hydrophobicity that are readily adsorbable by the sludge, the higher sludge concentrations, as well as probably higher extracellular polymeric substances (EPS) contents in the MBR, are conducive to the TrOPs' adsorption. For TrOPs that are less hydrophobic but still adsorbable by the particles and colloids in the mixed liquor, the MBR is potentially advantageous in rejecting these chemicals and improving the effluent quality. Overall, the removal efficiencies are jointly influenced by the mixed liquor properties (e.g., MLSS and EPS) and the operational conditions (such as SRT). TrOPs in the MBR system can undergo adsorption, degradation, rejection, and evaporation. They can be adsorbed by the bacterial cells, EPS, suspended solids, and colloids in the mixed liquor. After being adsorbed into the sludge phase, the pollutants may then undergo biodegradation. The MF or UF membrane has a marginal effect on the direct retention of TrOPs. However, the adsorption and size exclusion by the gel/cake layer are not negligible. The TrOPs can be readily rejected when they are adsorbed in the sludge phase or bound to colloids.
Exercise 13.4.9 | Exercise 13.4.9 | Describe the advantages of the MBR process in removing pathogens compared with other biological treatment processes. Which mechanisms do you think are behind its advantageous performance? | Membrane rejection is usually superior to gravitational settlement in bacteria removal. Compared with chemical disinfection technologies (such as chlorination, UV radiation, and advanced oxidation), membrane- based rejection of the pathogens is a gentle physical process that can bypass the risks of disinfection by- products, germ resistance, and involuntary mutations. MF or UF membranes can effectively reject protozoa, helminths, fungal spores, and bacteria, because their sizes are usually larger than the membrane pores.
Exercise 13.4.10 | Exercise 13.4.10 a | In an MBR process, what are the effects of the solids retention time (SRT) on mixed liquor properties? | MBR system, the long SRT is normally considered as an advantage, since a longer SRT results in higher biomass concentration, thus giving rise to a higher treatment efficiency.
Exercise 13.4.10 | Exercise 13.4.10 b | In an MBR process, If we extend the solids retention time (SRT) indefinitely until no sludge is discharged, how will the inorganic composition ratio of the sludge change and its influence on phosphorus removal? | A longer SRT also leads to the accumulation of inactive biomass and inorganic substances, thereby adversely affecting sludge activity. Generally, the sludge concentrations in the MBRs will increase with a longer SRT, whereas the ratio of volatile suspended solid to the total solid will decrease. However, for biological P removal, MBR acts like a double-edged sword. On the one hand, MBR can possess a high sludge concentration and a high P content per unit mass of sludge and the membrane can reject some of the colloidal P as well; on the other hand, the typically longer SRT (15-30 d) of MBR means a slower discharge of the excess sludge from the system.
Exercise 13.4.12 | Exercise 13.4.12 a | What are the main substances that cause fouling in an MBR-based process? | The main fouling-causing substances include polysaccharides, proteins, humic substances, and microorganisms and their cell debris.
Exercise 13.4.12 | Exercise 13.4.12 b | The main fouling-causing substances include polysaccharides, proteins, humic substances, and microorganisms and their cell debris, how can they be characterized? | These fouling-causing substances can be characterised using a series of advanced techniques. For example, the concentrations and functional groups of fouling-causing substances can be characterised using photometric methods, including UV-vis spectroscopy, excitation-emission matrix (EEM) fluorescence spectroscopy, and Fourier transform infrared (FTIR) spectroscopy. Fluorescence in situ hybridization coupled with confocal laser scanning microscopy (FISH–CLSM) and high-throughput sequencing technology can be used to characterise the microbial community of fouling-related microorganisms.
Exercise 13.4.12 | Exercise 13.4.12 c | The main fouling-causing substances include polysaccharides, proteins, humic substances, and microorganisms and their cell debris, describe their general roles in reversible and irreversible fouling. | Hydrophobic humic substances tend to adsorb to membranes, altering the surface properties of the membranes and narrowing membrane pores. As a result, the modified hydrophobic membrane surface facilitates the deposition of hydrophilic biomolecules, such as polysaccharides. This enhancement can be attributed to stronger interactions between polysaccharides and hydrophobic humic substances than those with hydrophilic membranes. In addition, the non-covalent network formed by proteins and polysaccharides has high membrane-fouling potential. Proteins and humic substances can also contribute to membrane fouling development via direct deposition in the bio-cake (reversible fouling) or the inter-molecule interactions. In particular, the presence of multi-valent cations in wastewater streams can considerably increase the gel layer formation (irreversible fouling) on membranes.
Exercise 13.4.13 | Exercise 13.4.13 a | List the methods widely used for assessing the filterability of mixed liquor. | A number of methods have been widely used for the assessment of filterability of mixed liquor, such as the critical flux determination by the flux-step method, Delft Filtration Characterization Method (DFCM), MBR-VITO fouling measurement, Berlin Filtration Method (BFM), and Sludge Filtration Index (SFI).
Exercise 13.4.16 | Exercise 13.4.16 a | Discuss the relationships between aeration scouring, sludge properties and membrane fouling. | Aeration is required in aerobic MBRs for providing DO to microbes, which puts the sludge flocs in a suspended state and mitigates membrane fouling. MBRs have a wide range of aeration rate, i.e., the specific aeration demand per membrane area in previous works ranged from less than 100 to over 1,000 l/h.m2. Generally, an increase in aeration intensity mitigates membrane fouling because it facilitates physical cleaning due to the increase in cross-flow velocity and shear stress. However, excessively high aeration increases both total and irreversible fouling rates. This is mainly attributed to the fact that the particle size distribution of the activated sludge shifts to lower size classes, and thus the concentrations of submicron particles, soluble microbial products, and biopolymers increase during high aeration. The shift of particle size to smaller flocs and fragments probably increases the total fouling resistance through the formation of a less permeable cake layer, while high concentrations of submicron particles probably increase irreversible fouling through pore blocking.
Exercise 13.4.16 | Exercise 13.4.16 b | Provide some feasible aeration modes for membrane fouling control that consume less energy. | Aeration optimization, including aeration rates, bubble size and aeration modes, is crucial in membrane fouling control. For instance, intermittent and pulsed aeration are efficient methods to control membrane fouling with less energy consumption. Also, high aeration during backwash and low aeration during filtration can greatly reduce the aeration demand compared with conventional MBRs. In addition, automatic aeration control is also of great interest for optimization of aeration.
Exercise 13.4.19 | Exercise 13.4.19 a | What are the differences between MBR and CAS processes in the design parameters for the biological section? | The major differences between the MBR and CAS processes are given below with explanations. The total SRT of MBR (15-30 d) is typically longer than that of CAS (10-20 d for a conventional AAO process). The MLSS concentration of MBR (6-15 g/l in the hollow-fibre membrane tank and 10-20 g/l in the flat- sheet membrane tank) is much higher than that of CAS (2.5-4.5 g/l in the aerobic zone). The MLVSS/MLSS proportion of MBR (0.4-0.7) is normally lower than CAS fed with the same wastewater. The synthesis yield of biomass of the MBR is similar to that of CAS (0.3-0.6 kgMLSS/kgBOD5), but the endogenous decay coefficient of MBR (0.05-0.2 1/d) is considered to be larger than that of CAS (0.04-0.075 1/d). The observed yield of solids of MBR (0.5-0.9 kgMLSS/kgBOD5, without primary sedimentation for instance) is thus designed to be slightly lower than that of CAS (0.6-1 kgMLSS/kgBOD5), considering the longer SRT and smaller sludge loading rate that facilitate endogenous decay. The maximum specific growth rate of nitrifying bacteria of MBR (~0.66 1/d) appears comparable with that of CAS, but the growth of nitrifying bacteria is facilitated by the longer SRT and can be more resilient at low temperatures in MBR than in CAS, which can influence the safety factor of the growth rate under these conditions.
Exercise 13.4.19 | Exercise 13.4.19 b | Why there are differences between MBR and CAS processes in the design parameters for the biological section? | The major differences between the MBR and CAS processes are given below with explanations. The total SRT of MBR (15-30 d) is typically longer than that of CAS (10-20 d for a conventional AAO process). This is because the membrane can completely reject suspended solids, which enables complete decoupling of SRT and HRT. A longer SRT facilitates the accumulation of nitrifying bacteria and increases TP content of the sludge. However, an excessively high SRT will restrict the excess sludge discharge, which is unfavourable for TP removal and will also lead to over-concentration of MLSS (especially inorganic MLSS), which impairs the operation of the system. The MLSS concentration of MBR (6-15 g/l in the hollow-fibre membrane tank and 10-20 g/l in the flat- sheet membrane tank) is much higher than that of CAS (2.5-4.5 g/l in the aerobic zone). This is due to the complete rejection of MLSS by the membrane and the long SRT of MBR. The sludge loading rate of MBR (0.03-0.1 kgBOD5/kgMLSS.d) is typically lower than that of CAS (0.05- 0.15 kgBOD5/kgMLSS.d), due to the higher MLSS concentration of MBR. The MLVSS/MLSS proportion of MBR (0.4-0.7) is normally lower than CAS fed with the same wastewater, because of the better degradation of the organics and the more complete membrane retention of inorganic MLSS in the MBR. The synthesis yield of biomass of the MBR is similar to that of CAS (0.3-0.6 kgMLSS/kgBOD5), but the endogenous decay coefficient of MBR (0.05-0.2 1/d) is considered to be larger than that of CAS (0.04-0.075 1/d). The observed yield of solids of MBR (0.5-0.9 kgMLSS/kgBOD5, without primary sedimentation for instance) is thus designed to be slightly lower than that of CAS (0.6-1 kgMLSS/kgBOD5), considering the longer SRT and smaller sludge loading rate that facilitate endogenous decay. The maximum specific growth rate of nitrifying bacteria of MBR (~0.66 1/d) appears comparable with that of CAS, but the growth of nitrifying bacteria is facilitated by the longer SRT and can be more resilient at low temperatures in MBR than in CAS, which can influence the safety factor of the growth rate under these conditions.
Exercise 13.4.20 | Exercise 13.4.20 a | Discuss the factors that could influence oxygen transfer and the alpha factor in an MBR system. | The factors that could influence the oxygen mass transfer coefficient (kLa) include aeration intensity, bubble size, diffuser submergence depth, biomass concentration and extracellular polymeric substances (EPS) content. The alpha factor is influenced by mixed liquor properties and aeration conditions. For coarse-bubble aeration, the alpha factor is jointly affected by MLSS concentration, EPS content and aeration intensity. For fine-bubble aeration, the alpha factor is heavily influenced by MLSS concentration.
Exercise 13.4.20 | Exercise 13.4.20 b | Discuss the implications from the factors that could influence oxygen transfer and the alpha factor in an MBR system for MBR design. | The factors that could influence the oxygen mass transfer coefficient (kLa) include aeration intensity, bubble size, diffuser submergence depth, biomass concentration and extracellular polymeric substances (EPS) content. The alpha factor is influenced by mixed liquor properties and aeration conditions. For coarse-bubble aeration, the alpha factor is jointly affected by MLSS concentration, EPS content and aeration intensity. For fine-bubble aeration, the alpha factor is heavily influenced by MLSS concentration. For the design of the biological section of an MBR process, the fine-bubble mode is usually adopted for biological aeration. Thus, the alpha factor can be estimated from the MLSS concentration in the aerobic zone (XO), using Equation 13.20 from Chen et al., 2020, i.e., α = 1.7exp(-0.08XO). Note that the parameters in this equation are very different from those for CAS cases because MBR is different from CAS in MLSS concentration and mixed liquor properties.
Exercise 13.4.21 | Exercise 13.4.21 | Discuss the factors that could render the excess sludge dewaterability of an MBR system different from that of a CAS system. | The excess sludge dewaterability can be influenced by multiple factors, especially the EPS content and physicochemical properties. Since MBR has longer SRT, higher MLSS concentration and a lower sludge loading rate, the microbial status and hence the EPS properties can be different from that of CAS. In addition, sludge bulking is tolerable for MBR operation due to complete rejection of the bacteria. The sludge dewaterability deteriorates if there is sludge bulking.
Exercise 14.3.1 | Exercise 14.3.1 a | Models are in essence a simplified representation of reality. How accurate should the models be? | A model never exactly reflects reality. It merely needs to be sufficiently complex and accurate to satisfactorily describe the main and most relevant conversion processes in order to achieve the purpose and objectives of the modelling study.
Exercise 14.3.1 | Exercise 14.3.1 b | Models are in essence a simplified representation of reality. Would a simpler but less accurate model be preferable to a complex and more accurate model? Explain your answer. | A model never exactly reflects reality. It merely needs to be sufficiently complex and accurate to satisfactorily describe the main and most relevant conversion processes in order to achieve the purpose and objectives of the modelling study.
Exercise 14.3.2 | Exercise 14.3.2 | What is the difference between a black-box model and a glass-box model? | A black-box model focuses on the plant influent and effluent with extremely limited (or no) involvement in or consideration of the processes happening inside the wastewater treatment units. Meanwhile, glass-box models have been developed to describe the metabolic routes inside the microorganisms. The application of either a black-box or a glass-box model depends very much on the purpose of the modelling study. For instance, black- box models (such as the ones based on the food to microorganisms (F/M) ratio) are good enough for the design of wastewater treatment systems. On the other hand, glass-box models (e.g., metabolic models) have proven to increase the understanding of certain conversion processes and, consequently, used to improve the design and performance of the systems (such as in the enhanced biological removal process).
Exercise 14.3.3 | Exercise 14.3.3 | A model is as accurate as the analytical methods used to determine its parameters. Is this true? Explain your answer and give a couple of supporting examples. | The required accuracy of the model depends on its purpose and application. Thus, the accuracy of the analytical methods influences the accuracy level of a model. For instance, to assess the effects of certain operating conditions on the sludge volume generated of a plant (often in tons of dry solids) or on the N2O emissions (in kgN/day), the main trends are sufficient and an exact fitting of the model outcomes is not needed in view of the expected accuracy of the analytical determination methods. However, if the purpose is to model, for example, the ammonium effluent concentrations to meet an effluent discharge standard of less than 1 mgNH4-N/L, then the analytical determination of ammonium needs to be more precise and the model accuracy (and likely also its complexity) be high enough to describe such ammonium concentrations.
Exercise 14.3.6 | Exercise 14.3.6 | For ASM1, the biodegradable COD in influent consists of two fractions. Give the name and abbreviation of these two fractions. What does iNXs stand for? | Ss (soluble biodegradable COD) and Xs (particulate biodegradable COD). iN,Xs is the nitrogen concentration related to or present in the particulate organic substrate Xs.
Exercise 14.3.7 | Exercise 14.3.7 a | In ASM1, the stoichiometric coefficients of the process matrix for aerobic and anoxic growth of ASM1 can be calculated by setting up mass balances. Which three compounds can be balanced? | The three compounds that can be balanced are COD, N and charge.
Exercise 14.3.7 | Exercise 14.3.7 b | In ASM1, the stoichiometric coefficients of the process matrix for aerobic and anoxic growth of ASM1 can be calculated by setting up mass balances. Give three aspects that affect the conversions in the activated sludge but are not described by the activated sludge model. | Three parameters or factors that affect the conversions but that are not included in the model are pH, toxicity and diffusion.
Exercise 14.3.7 | Exercise 14.3.7 c | In ASM1, the stoichiometric coefficients of the process matrix for aerobic and anoxic growth of ASM1 can be calculated by setting up mass balances. Which is the most important compound to be measured to evaluate the model? | Oxygen is the most important parameter that needs to be measured to evaluate the compartment model.
Exercise 14.3.9 | Exercise 14.3.9 | Why is nitrite left out of the ASM1 model? | Most plants run at lower temperatures (< 20 o C), nitrite will remain very low, so from a mass balance perspective there is no need to take it into account. In the case of higher temperature or toxic events, nitrite might accumulate.
Exercise 14.3.10 | Exercise 14.3.10 a | When representing the hydraulics of the aeration tank in a full-scale WWTP, which compounds need to be measured across the tank? | Oxygen, ammonium, nitrate and phosphate.
Exercise 14.3.10 | Exercise 14.3.10 b | When representing the hydraulics of the aeration tank in a full-scale WWTP, Under what conditions can the tank in the model be considered as fully mixed? | When there are no concentration gradients measured.
Exercise 14.3.11 | Exercise 14.3.11 | Explain the role of the switching function in the model. Give an example of a switching expression used in the ASM1 model and explain how it works. | A switching function is a saturation term (of the type S / (K + S)) whose main purpose is to stop a process when a relevant compound is no longer present. As an example, if an ammonia switching function of the type SNH / (KNH,OHO + SNH) is used in an expression that describes the growth process of ordinary heterotrophic organisms (with a relatively low value for the half-saturation concentration KNH,OHO of, for instance, less than 0.1 mgN/l), it will tend to a value of 1.0 at the usual concentrations observed in activated sludge systems (usually higher than 4-5 mg/l in the effluent of the plant): SNH / (KNH,OHO + SNH)) = 4 / (0.1 + 4) ≈ 1.0. This will not limit or hinder the growth of ordinary heterotrophic organisms (as far as other relevant compounds are still present). However, if ammonia is fully removed and not present anymore, the result of the expression will be 0 (0 / (0.1 + 0) = 0), stopping the growth process. Often, switching functions are mixed up with relevant saturation expressions and the differentiation between them is rather vague. Nevertheless, when the values of the half-saturation concentrations K are real parameters (calculated or estimated based on actual data to describe a conversion process in particular when the compound of interest tends to be limiting) the expression is a saturation term. On the other hand, when K is empirically assigned without looking into its influence on the conversion but only to stop the process, the expression is a switching function.
Exercise 14.3.12 | Exercise 14.3.12 a | Why are modern models COD-based (and not BOD-based)? | Modern models are based on the chemical oxygen demand (COD) and not on the biochemical oxygen demand (BOD) because COD makes it possible to perform a mass balance of the organic compounds, including the unbiodegradable organic compounds, present in the wastewater influent or generated during or from the biological conversion processes. This is also because the COD by definition measures the electron-donating capacity transferred to oxygen in order to oxidize the biodegradable organics. This makes it possible to precisely calculate the oxygen required for the aerobic processes to take place. On the other hand, the BOD technique is lengthy (it lasts at least 5 days, while the COD can be performed in 2 h) and rather sensitive to the influence of different factors (such as temperature, biodegradability, presence of toxic compounds) that can make it impossible to perform and track the conversion processes.Furthermore, the COD mass balance can be applied to revise the correctness and accuracy of the organic matter removal models and calculate unknown stoichiometric parameters and values. This makes it a robust and reliable tool for modelling purposes.
Exercise 14.3.12 | Exercise 14.3.12 b | Why is the oxygen concentration in ASM models expressed as a negative value of COD? | This is also because the COD by definition measures the electron-donating capacity transferred to oxygen in order to oxidize the biodegradable organics. This makes it possible to precisely calculate the oxygen required for the aerobic processes to take place.
Exercise 14.3.14 | Exercise 14.3.14 | List the seven main steps to build a model for a wastewater treatment plant. | Definition of the model purpose or objectives of the simulation study. 2. Model selection: choice of models needed to describe the different plant units to be considered in the simulation, e.g., selection of the activated sludge model, the sedimentation model, etc. 3. Hydraulics, i.e., determination of the hydraulic models for the plant or plant components. 4. Wastewater and biomass characterization, including biomass sedimentation characteristics. 5. Calibration of the sludge model parameters. 6. Model verification. 7. Scenario evaluations.
Exercise 14.3.15 | Exercise 14.3.15 | It is unlikely that the first simulation will provide the user with the satisfactory results. This means that the user needs to calibrate the model. Which parameters of interest are usually calibrated in a biological nutrient removal (BNR) model, in which order? | Given that the influent characteristics, fractionation and hydraulics are correctly determined: 1. The aerated and non-aerated (anaerobic and anoxic) sections need to be well defined. 2. The solids retention time (SRT) needs to be adjusted or calibrated to describe the actual mixed liquor suspended solids concentration in the system and the sludge production; for this purpose, the phosphorus balance can be used. 3. The COD balance, including the effluent concentrations, needs to be adjusted. 4. The nitrogen (TKN) content present in the sludge waste needs to be adjusted to account for the actual nitrogen requirements for biomass synthesis. 5. The actual DO concentrations in the tanks need to be adjusted and assessed to describe the ammonia and nitrate concentrations in the treatment units and internal recirculation flows. 6. If the nitrogen profiles are not yet satisfactorily described, the maximum aerobic and anoxic kinetic rates of nitrifiers and denitrifiers and the anoxic kinetics of polyphosphate accumulating organisms (PAO), also their half-saturation concentrations (mostly for oxygen and key substrates) can be adjusted to fit the nitrogen balance (N load and denitrification). 7. The aerobic kinetic rates of PAO need to be adjusted to match the aerobic phosphorus profiles and the phosphorus content present in the sludge waste (also to assess whether the plant may have chemical P removal). For further details, refer to Meijer and Brdjanovic, 2012.
Exercise 14.3.16 | Exercise 14.3.16 | If your treatment plant is not designed for biological phosphate removal, would you still apply the activated sludge model that includes a bio-P removal on a non-bio-P plant? Explain your answer. | Strictly speaking, if the plant is not designed to perform the enhanced biological phosphorus removal (EBPR) process, it is not necessary to use a model that considers the EBPR conversion processes because this will make the model more complex and modelling more demanding. However, inclusion of a bio-P component of the model is recommended because the model P balance gives a check on the data accuracy (since P is a conserved element), and SRT and sludge production.
Exercise 14.3.18 | Exercise 14.3.18 a | In some locations treated effluents are not disinfected, and therefore not free of pathogens, due to safe effluent discharges and restricted access to discharge points and receiving water bodies. However, in other regions, there is a need for pathogen removal from wastewater. ASM models do not include pathogen removal. Which pathogens should be included as indicators of faecal contamination? | Current ASM models do not include the expressions required to assess the inactivation of pathogens because conventional wastewater treatment systems hardly contribute to the removal of pathogens (besides certain natural systems, such as maturation ponds). For pathogen inactivation, ASM models need to be expanded to describe the disinfection processes that can take place in post-treatment units. Most of these systems are designed and operated as plug-flow reactors exposed to different types of disinfectant agents. The most common disinfection processes are chlorine (not recommended due to potential associated health issues), UV and ozone (O3). The disinfection processes driven by these disinfectants could be incorporated in the ASM models to describe the disinfection of selected key pathogens. For example, regarding faecal contamination, the inactivation of faecal coliforms could be incorporated. For other purposes and depending on the potential (re)use of the treated and disinfected effluents, other indicators could be added (e.g., helminth eggs for irrigation purposes).
Exercise 14.3.18 | Exercise 14.3.18 b | In some locations treated effluents are not disinfected, and therefore not free of pathogens, due to safe effluent discharges and restricted access to discharge points and receiving water bodies. However, in other regions, there is a need for pathogen removal from wastewater. ASM models do not include pathogen removal. How would pathogen removal be modelled? | To incorporate pathogen removal, decay or inactivation, one or more mathematical equations will need to be incorporated in the model.
Exercise 14.3.18 | Exercise 14.3.18 c | In some locations treated effluents are not disinfected, and therefore not free of pathogens, due to safe effluent discharges and restricted access to discharge points and receiving water bodies. However, in other regions, there is a need for pathogen removal from wastewater. ASM models do not include pathogen removal. Which factors could influence and therefore be included for model pathogen removal from wastewater? | The factors that influence the disinfection processes will need to be incorporated as well to provide an adequate description. These include, among others, the influence of suspended solids, pH and temperature. Also, certain processes will be process-dependent such as the hindrance caused by the suspended solids for UV disinfection and the gas-transfer expressions required to model the ozone supply.
Exercise 15.4.1 | Exercise 15.4.1 a1 | An activated sludge process is provided with several recirculation flows. Discuss the consequences of too low return sludge flowrates. Note that the consequences can be both hydraulic and influence concentrations. | A too-low return sludge flow rate can cause the sludge level to rise too much. Therefore, it is favourable to measure the sludge blanket level and control accordingly.
Exercise 15.4.1 | Exercise 15.4.1 a2 | An activated sludge process is provided with several recirculation flows. Discuss the consequences of too high return sludge flowrates. Note that the consequences can be both hydraulic and influence concentrations. | Return sludge: a high-return sludge can influence the settler performance, in particular when the return sludge flow rate is very high. The sludge level will decrease or disappear.
Exercise 15.4.1 | Exercise 15.4.1 b | An activated sludge process is provided with several recirculation flows. Discuss the consequences of too high flowrates of backwashing from effluent polishing filters. Note that the consequences can be both hydraulic and influence concentrations. | Backwashing: this often causes a sudden high hydraulic flow rate change in the plant inlet. It is important to make sure that the backwash flow can be stored temporarily and not returned to the inlet when there are high loads. Feedforward control from the filtering process to the plant influent could be considered.
Exercise 15.4.1 | Exercise 15.4.1 c | An activated sludge process is provided with several recirculation flows. Discuss the consequences of too low flowrates of reject flow from anaerobic sludge treatment back to the influent of the activated sludge process. Note that the consequences can be both hydraulic and influence concentrations. | Anaerobic sludge: this usually provides a high ammonia peak load. Therefore, the sludge load should be provided at low plant influent loads.
Exercise 15.4.3 | Exercise 15.4.3 a | It is important to handle hydraulic disturbances correctly. Suppose that a relatively large increase appears inthe influent water flow rate. Explain what would happen if there is no control action taken (in the aerator or in the settler units). | A large increase in the influent water flow will have two major impacts. Firstly, the residence time in the reactor will be shorter, which will lead to the risk of incomplete reaction time. Secondly, in extreme cases, it can result in washout. The flow rate of change will have a hydraulic impact on both the settler and clarifier (the two separate operations in the same settler unit) and create a turbulent flow, which can cause sludge washout.
Exercise 15.4.3 | Exercise 15.4.3 b | It is important to handle hydraulic disturbances correctly. Suppose that a relatively large increase appears inthe influent water flow rate. Suppose that you know a few hours ahead that this flow increase will happen. How would you prepare the plant for the disturbance? | By being able to predict an increasing flow rate it might be possible to offset the flow rate impact onthe plant by using an equalization basin. The main sewer can serve as such a basin to store the influent flow temporarily.
Exercise 15.4.4 | Exercise 15.4.4 | List possible differences in disturbance patterns in different plant types, such as: a) small municipal plants with mostly domestic waste, b) small municipal plants with a major industry connected, c) large municipal plants with mostly domestic waste, d) large municipal plants connected to industries. Consider their sources, their likely frequency, and magnitude. | Usually, a large plant connects to a wider sewer network, compared to a small plant. Therefore, load variations in a small plant can be larger than those in a large plant. If industries are connected to the plant, their impact depends on the type of industry. Sometimes there will be a major industry connected to a small plant. For example, a large brewery or slaughterhouse can create large organic disturbances. On the other hand, if they are connected to a large plant, their impact is typically lower.
Exercise 15.4.5 | Exercise 15.4.5 a | List possible consequences of too much of the dissolved oxygen for denitrification | In the anoxic zone the denitrification is hindered by too much DO
Exercise 15.4.5 | Exercise 15.4.5 b | List possible consequences of too much of the dissolved oxygen for nitrification | In the aerator high DO favours a high nitrification rate
Exercise 15.4.5 | Exercise 15.4.5 c1 | List possible consequences of too little of ammonia for principal biological nutrient removal processes? | Too little ammonia means that the activity of the microorganisms will decrease and hence over time the concentration of the bacteria can also decrease due to the low availability of 'food'. This can appear in industrial effluents, for example in the paper and pulp industry. Then nutrients have to be added. In municipal treatment, this rarely happens.
Exercise 15.4.5 | Exercise 15.4.5 c2 | List possible consequences of too much of ammonia for principal biological nutrient removal processes? | If too much ammonia enters the plant, the aeration capacity might be too small. Similarly, the nitrification capacity can be reduced if influent water temperature is low and/or it contains toxic substances.
Exercise 15.4.6 | Exercise 15.4.6 | Give two examples of changes in process conditions that can affect the clarification and thickening processes. | a. The microbial sludge composition can influence both settling and clarification properties. If there are filamentous or free-swimming organisms, then the floc properties are unfavourable for settling and clarification. Typically, a too-low DO concentration in the aerator can inhibit the floc formation. b. On-off influent pump operation instead of smooth operation can disturb clarification by causing unwanted turbulence in the settler.
Exercise 15.4.7 | Exercise 15.4.7 | Assume that the influent flow rate is suddenly increased by 20 % due to a pump starting. Discuss how this flowrate change will manifest in the wastewater treatment system, and how various unit operations can be influenced. The timescale is important. | There are two different kinds of response. Firstly, as the influent flow rate suddenly increases, a 'hydraulic shock wave' will propagate along the plant. An increase in flow rate in the plant inlet will propagate some 20- 40 minutes later (depending on the size of the plant) to the plant outlet. This in turn can have an impact on the clarifier operation. The second response relates to the decreasing retention time in the reactors. This will influence how the reactions manage to reach their completion. If sludge recirculation and internal recirculation are controlled proportionally to the influent flow rate, this can further amplify the impact of a flow-rate step change throughout the plant.
Exercise 15.4.8 | Exercise 15.4.8 | We talk about 'data rich' and 'information poor'. Suppose that you see the record of a variable which is a straight line. Is that data information-rich? | This depends on the circumstances. Generally, a straight line contains very little information. The sensor might have got stuck on a value. Usually large or small variations in a value contain more information. However, if the line is due to good control of e.g. DO, this is evidence of very good control. In this case the airflow rate isa good indicator of the reactor load. A competent observer can convert data to rich information just by looking at the graphics.
Exercise 15.4.9 | Exercise 15.4.9 | Explain in words the difference between a low-pass and a high-pass filter. | a. Low-pass signal filtering will remove higher signal frequencies, such as noise, while retaining the essential signal information – it smooths the signal and makes it easier to see the general trend of the data. However, be aware that in the case of online filters, more smoothing results in more delay of the signal content. b. High-pass filters remove low signal frequencies and can be used to detect changes in a signal (like a derivative). In this way, sudden or fast changes can be detected.
Exercise 15.4.10 | Exercise 15.4.10 | Noise is defined as the measurement component that does not contain any information. However there are cases when noise contains information that helps to detect faults. Explain! | Any sensor can present a noisy signal. For example, if a membrane becomes fouled, then the appearance of the noise can look different than if the membrane is clean. Automatic analysis of the noise character can reveal if it is time to clean the sensor. Noise is generally defined by being random, but occasionally, what at first glance appears random can contain some patterns, which means that some pattern can be recognized. Understanding this process can be valuable.
Exercise 15.4.11 | Exercise 15.4.11 a | Where is the best location for an ammonia sensor for control purposes? | Ammonia sensor: mostly the last aeration zone is used. The sensor can also be placed in the effluent, which has a more favourable environment. Then the response time is longer but also more representative of the effluent water quality (for legislative purposes). Ammonia sensors can also be placed close to the inlet to create a feedforward signal, but this is not common.
Exercise 15.4.11 | Exercise 15.4.11 b | Where is the best location for a nitrate sensor? | Nitrate sensor: this should be located close to the outlet of the anoxic zone.
Exercise 15.4.11 | Exercise 15.4.11 c | Where is the best location for a phosphate sensor for chemical precipitation? | A phosphate sensor for chemical precipitation ought to be located in the effluent of the flocculation chamber. The retention time in the flocculation chamber is short, typically around one hour, which is much shorter than the timeframe of phosphate variations in the chemical step. Chemical dosage can be based on feedback from this sensor.
Exercise 15.4.12 | Exercise 15.4.12 | Why is it often favourable to combine feedforward with feedback? Explain what is needed to obtain a successful feedforward. | The idea of feedforward is to measure a disturbance before it reaches the plant, for example, an increasing influent flow rate or an ammonia increase. If we know exactly how this disturbance is going to influence the plant, then the influence of the disturbance can be cancelled by the right actions. This is the idea of feedforward. However, we hardly ever have exact knowledge about how a disturbance influences the plant, since our model is not perfect. Therefore, we also need to measure the outcome of the disturbance, for example the effluent ammonia concentration, which is a feedback operation. Feedback then acts as a correction of a non-perfect feedforward. So, feedforward creates a quick but non-perfect correction to deal with a disturbance, while feedback will make an accurate but slower final correction. Controller tuning is critical in terms of both feedforward and feedback. A well-tuned feedforward control makes it possible to use a feedback controller which has been tuned to operate slowly, which reduces the risk of instabilities.
Exercise 15.4.14 | Exercise 15.4.14 a | Consider some nonlinear phenomena in process control of wastewater treatment systems. Give examples of nonlinear effects/terms in the DO dynamics. | The oxygen transfer rate kLa is not proportional to the airflow rate. Therefore, it is nonlinear. At a low load, the kLa will increase more for an airflow increase compared to the case at a high load. Another nonlinearity is the factor DOsat-DO that appears in the oxygen transfer term.
Exercise 15.4.14 | Exercise 15.4.14 b | Consider some nonlinear phenomena in process control of wastewater treatment systems. What could be the effect of these nonlinearities if the DO is automatically controlled? | A DO controller will typically react more sensitively at a low load than at a high load. Additionally, Monod kinetics make the process rates non-linearly dependant on DO concentrations – this is the case for nitrification, denitrification as well as conversion of organic matter. A consequence of the different process gains at low and at high loads can cause oscillatory behaviour in some cases.
Exercise 15.4.14 | Exercise 15.4.14 c | Consider some nonlinear phenomena in process control of wastewater treatment systems. Is there a way to reduce the effect of the nonlinearities on the control system? | A remedy for these non-linearities is called gain scheduling. This is a way to automatically change the controller gain according to the size of the manipulative variable (control signal).
Exercise 15.4.14 | Exercise 15.4.14 d | Consider some nonlinear phenomena in process control of wastewater treatment systems. What type of nonlinearity occurs typically in a control valve? | Another nonlinearity usually appears in valves. The flow rate may not be proportional to the valve opening. For example, the flow rate change is different for a valve opening change when the valve is almost fully closed compared to when it is almost fully open.
Exercise 15.4.15 | Exercise 15.4.15 | Suppose that a too-low DO level is detected in an aerator with closed loop DO control. What kind of causes should you look for? | Check the followings: 1) is the DO sensor calibrated? 2) are the blowers operating with full capacity? 3) is the airflow valve operating, or is it stuck in a position?
Exercise 15.4.16 | Exercise 15.4.16 a | A toxic load enters an aerator that has automatic DO control. How can the DO control system detect the toxic load? | In principle, a decreasing load and a toxic disturbance will have a similar impact on the oxygen demand, so the DO controller cannot distinguish between the two.
Exercise 15.4.16 | Exercise 15.4.16 b | Can the DO control system distinguish between a toxic disturbance and other load changes? | Sometimes the timescale is different. If the oxygen demand decrease appears to be much quicker than a typical load decrease, this can be a probable reason for a toxic alarm.
Exercise 15.4.18 | Exercise 15.4.18 | Suppose that the DO level rises to about 9-10 mg/l from the normal operating range of 1-3 mg/l within a minute. What could be the reason? | This happens if the operator takes the DO sensor into the open air for a calibration check or cleaning. Subsequently, the DO control system should include a test; if the DO concentration increases at a certain speed, then the control system should keep the airflow constant until more normal DO concentrations are observed.
Exercise 15.4.19 | Exercise 15.4.19 | In a nitrogen removal plant the effluent standard often defines a limit on the total nitrogen out of the plant, i.e. the sum of ammonia N and nitrate N. In the operation of an N removal plant there is always a compromise on how to obtain minimum effluent total N. Discuss how to control the plant so that we will satisfy the total N condition and still save as many resources as possible. | Bear in mind that nitrification has to occur before denitrification. This is the case both in pre-denitrification and in post-denitrification plants. So, we have to balance between oxidizing ammonia to nitrate and reducing nitrate N to nitrogen gas via denitrification. To oxidize ammonia N to nitrate N using nitrification is usually more expensive, since it requires energy for aeration. Normally it is cheaper to remove nitrate N using denitrification. In a pre-denitrification plant, there must be a sufficient carbon source, which in most cases is supplied by the BOD/COD in the influent. In a post-denitrification plant, external carbon has to be added because the BOD/COD has been biologically degraded by oxidation. The cost of external carbon should be compared with the cost of aeration. It is usually cheaper to reduce as much nitrate as possible and to minimize oxidation of ammonia.
Exercise 16.4.1 | Exercise 16.4.1 a | Explain what anaerobic digestion is. | Anaerobic digestion (AD) is a mineralization process in which carbon acts both as electron donor and electron acceptor (redox reaction) and organic matter is eventually converted into the most oxidized and most reduced form of carbon, i.e., a mixture of CO2 and CH4, also called biogas.
Exercise 16.4.1 | Exercise 16.4.1 b | Explain what are the redox potentials associated to anaerobic digestion. | This process occurs under reducing conditions and, therefore, negative potentials reaching -300 to -500 mV are required for the reactions to proceed.
Exercise 16.4.2 | Exercise 16.4.2 | List six advantages of anaerobic over aerobic wastewater treatment methods. | 1) No energy is required for the main reactions to occur, e.g., avoidance of aeration and therefore aeration equipment. 2) Energy can be recovered in the form of biogas. 3) Minimal excess sludge production (reduction of up to 90%). 4) Sludge produced is already stabilized. 5) Compact reactor system owing to high applicable COD loading rates reaching 20-35 kgCOD/m3 . 6) Nutrients such as ammonium (NH4 + ) and phosphate (PO4 -3 ) remain in the treated wastewater for possible recovery, e.g., in ferti-irrigation.
Exercise 16.4.4 | Exercise 16.4.4 a | Give an example of an acetogenic conversion reaction . | CH3CH2CO2- + 3H20 → CH3COO- + HCO3- + H+ +3H2
Exercise 16.4.4 | Exercise 16.4.4 b | Explain why acetogenic conversion reaction is the most difficult step in the entire digestion chain. | CH3CH2CO2- + 3H20 → CH3COO- + HCO3- + H+ +3H2 For instance, the propionate acetogenic reaction has a positive Gibb's free energy change of +76 kJ/mol and thus cannot proceed spontaneously. This is the most difficult step in the reaction because it only proceeds when H2 is continuously removed from the solution, improving the reaction's thermodynamics, by lowering the Gibb's free energy change to negative values.
Exercise 16.4.5 | Exercise 16.4.5 | Describe three differences between archaea and bacteria. | Some archaea, such as acetoclastic and hydrogenotrophic methanogens, produce methane, but bacteria cannot. 2) Bacteria contain peptidoglycan in the cell wall whereas archaea do not (they mainly contain pseudopeptidoglycan). 3) Bacterial cell membrane mainly consists of fatty acids with ester bonds whereas archaeal cell membrane contains phytanyls linked through ether bonds.
Exercise 16.4.7 | Exercise 16.4.7 | Explain the differences between COD and BOD. | COD stands for chemical oxygen demand. During the analysis all substances are measured that can be oxidized using a strong oxidant (dichromate). Both biodegradable and unbiodegradable matter is oxidized. Although more substances can be oxidized, the COD is mostly related to the organic compounds in a sample. It is important to remember that NH4 + is not oxidized and nor are quaternary ammonium salts, such as betaine. Experimentally, it is a quick test with an average duration of 3-4 h. BOD stands for biochemical oxygen demand. It is a measurement of the quantity of substances, mainly organic matter, which can be oxidized by bacteria under aerobic conditions. This measurement considers only biodegradable matter, while NH4 + can also be oxidized. BOD is a lengthy test that usually takes 5, 7 or 10 days.
Exercise 16.4.10 | Exercise 16.4.10 a | List three of the most common electron acceptors that can be found in wastewater (apart from oxygen). | The ions sulphate (SO4 2-), nitrate (NO3 - ), and oxidized iron (Fe3+).
Exercise 16.4.10 | Exercise 16.4.10 b | Explain how the most common electron acceptors (apart from oxygen) affect the methanogenic process. | The presence of sulphate (SO4 2-), nitrate (NO3 - ), and oxidized iron (Fe3+) will decrease the methane production.
Exercise 16.4.10 | Exercise 16.4.10 c | Explain why the most common electron acceptors (apart from oxygen) affect the methanogenic process. | The ions sulphate (SO4 2-), nitrate (NO3 - ), and oxidized iron (Fe3+) will decrease the methane production because thermodynamically, these molecules are better electron acceptors than carbon (C), meaning that e.g., sulphate-reducing bacteria will outcompete methanogens in an anaerobic reactor and nitrate reduction can even completely halt methanogenesis.
Exercise 16.4.12 | Exercise 16.4.12 | List four of the main problems found in anaerobic reactors when the influent to be treated has a high concentration of sulphate. | Methanogens can become toxified by high hydrogen sulfide (H2S) concentrations. 2) The metallic parts of the reactors and pipelines corrode due to H2S. 3) There is a decrease in the biogas quality due to the presence of H2S. 4) There are bad odours in the vicinity of the reactor, due to the presence of hydrogen sulphide (H2S).
Exercise 16.4.17 | Exercise 16.4.17 | List the two most important conditions required to achieve biomass granulation in a reactor. | 1) Dosage/feeding of the reactor with soluble substrates. 2) Reactor operation in an upflow mode with short hydraulic retention times.
Exercise 16.4.18 | Exercise 16.4.18 | Explain and schematize the granulation process mechanism. | 1) Nuclei growth, usually on inert organic or inorganic carriers. It is possible that the microorganisms aggregate in other already existing bacterial conglomerates. 2) Film or aggregate formation and wash out of dispersed matter including microorganisms that were not retained in the granules. 3) Formation of the 'first generation of granules'. These aggregates are mainly filamentous granules, voluminous and somewhat flocculent. 4) Growth of the secondary nuclei, both in size and bacterial density. 5) Aging or 'maturation' of the granules. In this step, compact and denser granules will displace the filamentous granules found in the initial stages.
Exercise 16.4.19 | Exercise 16.4.19 | List the main features of a reactor that is considered to be an HRAR system. | 1) High retention of viable sludge in the reactor under operational conditions. 2) Sufficient contact between viable bacterial biomass and wastewater. 3) High reaction rates and absence of serious transport limitations. 4) Sufficient adaptation by the biomass to the prevailing conditions in the reactor. 5) Prevalence of favourable environmental conditions for all the required microorganisms in the reactor.
Exercise 16.4.28 | Exercise 16.4.28 a | Give five advantages of applying AD for the treatment of municipal wastewater. | 1) Savings of up to 90 % in operational cost, no aeration needed. 2) 40 to 60 % reduction in investment costs as a simpler treatment train is needed. 3) Possibility of energy recovery as methane. 4) Reactor configurations that allow decentralized schemes. 5) A well-designed reactor, such as a UASB reactor, can partly filter helminth eggs.
Exercise 16.4.28 | Exercise 16.4.28 b | Give five constraints of applying AD for the treatment of municipal wastewater. | 1) Requirement of a polishing post-treatment. 2) Dissolved CH4 in the effluent that will eventually escape into the atmosphere. 3) The CH4 is not usually recovered or flared. 4) Little experience with full-scale application at moderate temperatures. 5) Other reduced gases such as H2S may escape, causing odour problems in the vicinity of the treatment plant.
Exercise 16.4.30 | Exercise 16.4.30 | Explain the effect of temperature on the SRT of the anaerobic reactors. | There is an inverse relationship between the operating temperature and the required SRT. This effect is because, as a rule of thumb, the SRT should be at least 3 times the doubling time of the biomass responsible for the rate-limiting step, which can be either the methanogens or the hydrolytic bacteria. When the temperature in the reactor is increased, the reaction and growth rates become higher, therefore decreasing the required time for sludge stabilisation or mineralisation. However, there is a maximum limit for the operating temperature, which is linked to the maximum temperature span of the respective organisms. Raising the temperature beyond the maximum temperature results in net decay.